## Registers & Files
| Starting Address | Ending Address | Modbus Function Code | Register / File Description | # Items | Registers per Item | Total # Bytes | Total # Registers | Range | Access Type | NF500 Writers (Init Task writes all) | NF500 Readers (Modbus Slave TX reads all) | NF3500 | Note
0xxxx "Discrete Input" (Bit)
| 1 |  |  | Terminal Defined Configuration
0xxxx | 1 | 17 | 01,02 | Terminal Defined Control , Terminal 1 - 16 | 16 | 1 | 2 |  | 0 = inactive, 1 = active* | RD/CW |  |  | x
| 21 |  |  | Terminal Active Configuration
0xxxx | 21 | 36 | 01,02 | Terminal Active Control , Terminal 1 - 16 | 16 | 1 | 2 |  | 0 = inactive, 1 = active* | RD/CW |  |  | x
| 41 |  |  | Input Defined Configuration
0xxxx | 41 | 296 | 01,02 | Input Defined Control , Inputs 1 - 256 | 256 | 1 | 32 |  | 0=undefined, 1=defined, default:1-16 =1, 17-256 = 0 | RD/CW |  |  | x
| 301 |  |  | Input Active Configuration
0xxxx | 301 | 556 | 01,02 | Input Active Control , Inputs 1 - 256 | 256 | 1 | 32 |  | 0=inactive, 1=active, default:1-16 =1, 17-256 = 0 | RD/CW |  |  | x
| 1201 |  |  | Input Manual Control
0xxxx | 1201 | 1456 | 01,02 | Latched Input State Control Manual, Inputs 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
| 1501 |  |  | Input Auto Control
0xxxx | 1501 | 1756 | 01,02 | Latched Input State Control, Auto, Inputs 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
| 1801 |  |  | Input - Terminal Inhibit Control
0xxxx | 1801 | 2056 | 01,02 | Input Inhibit, Inputs 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
| 2101 |  |  | Input Timer Inhibit Control
0xxxx | 2101 | 2356 | 01,02 | Input Timer Inhibit, Inputs 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
| 3001 |  |  | Zone Defined Configuration
0xxxx | 3001 | 3256 | 01,02 | Zone Defined Control , Zones 1 - 256 | 256 | 1 | 32 |  | 0=undefined, 1=defined, default:1-16 =1, 17-256 = 0 | RD/CW |  |  | x
| 3301 |  |  | Zone Active Configuration
0xxxx | 3301 | 3556 | 01,02 | Zone Active Control , Zones 1 - 256 | 256 | 1 | 32 |  | 0=inactive, 1=active, default:1-16 = 1, 17-256 = 0 | RD/CW |  |  | x
| 3601 |  |  | Zone Manual Control
0xxxx | 3601 | 3856 | 01,02 | Zone Manual Control, Zones 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
| 3901 |  |  | Zone Auto Control
0xxxx | 3901 | 4156 | 01,02 | Zone Auto Control, Zones 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
| 4201 |  |  | Zone Override Enable
0xxxx | 4201 | 4456 | 01,02 | Zone Override Enable, Zones 1-256 | 256 | 1 | 32 |  | 0 = release*, 1 = enable | RD/WR |  |  | x
| 4501 |  |  | Zone Override Type
0xxxx | 4501 | 4756 | 01,02 | Zone Override Type, Zones 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
| 4801 |  |  | Remote Source Control
0xxxx | 4801 | 4864 | 01,02 | Remote Source State, 1 - 64 | 64 | 1 | 8 |  | 0 = OFF*, 1 = ON | RD/CW |  |  | x
| 4901 |  |  | Remote Source Auto/Manual
0xxxx | 4901 | 4964 | 01,02 | Remote Source Auto/Manual, 1-64 | 64 | 1 | 8 |  | 0 = auto*, 1 = manual | RD/CW |  |  | x
| 5001 |  |  | Remote Source Defined Configuration
0xxxx | 5001 | 5128 | 01,02 | Remote Source State, 1 - 128 | 128 | 1 | 16 |  | 0 =undefined, 1 = defined | RD/CW |  |  | x
| 5131 |  |  | Remote Source Active Configuration
0xxxx | 5131 | 5258 | 01,02 | Remote Source Auto/Manual, 1-128 | 128 | 1 | 16 |  | 0 = inactive*, 1 = active | RD/CW |  |  | x
| 5501 |  |  | System Control
0xxxx | 5501 | 5501 | 01,02 | Front Panel Disable | 1 | 1 | 0.125 |  | 0 = normal*, 1 = disable keys | RD/CW |  |  | x
0xxxx | 5502 | 5502 | 01,02 | Halt Mode Enable | 1 | 1 | 0.125 |  | 0 = normal*, 1 = halt | RD/CW |  |  | x
0xxxx | 5503 | 5503 | 01,02 | Learn Mode Enable | 1 | 1 | 0.125 |  | 0 = normal*, 1 =enable learn | RD/CW |  |  | x
0xxxx | 5504 | 5504 | 01,02 | SNTP Enable | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5505 | 5505 | 01,02 | Test Mode | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5506 | 5506 | 01,02 | Email Enable | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0
0xxxx
0xxxx
0xxxx
0xxxx
0xxxx
| 5601 |  |  | Global Event Enable
0xxxx | 5601 | 5601 | 01,02 | Event Enable, Not Used | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5602 | 5602 | 01,02 | Event Enable, Input Object | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5603 | 5603 | 01,02 | Event Enable, Zone Object | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5604 | 5604 | 01,02 | Event Enable, ZoneOverride Object | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5605 | 5605 | 01,02 | Event Enable, Configuration Mode | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5606 | 5606 | 01,02 | Event Enable, Firmware Download | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5607 | 5607 | 01,02 | Event Enable, Special Day Object | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5608 | 5608 | 01,02 | Event Enable, Schedule Object | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5609 | 5609 | 01,02 | Event Enable,Direct Breaker Control Object | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5610 | 5610 | 01,02 | Event Enable, Learn Mode | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5611 | 5611 | 01,02 | Event Enable, Reset | 1 | 1 | 0.125 |  | always enabled | RD |  |  | x
0xxxx | 5612 | 5612 | 01,02 | Event Enable, Bus Present | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5613 | 5613 | 01,02 | Event Enable, Breaker Present | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5614 | 5614 | 01,02 | Event Enable, Remote Source Objects | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5615 | 5615 | 01,02 | Event Enable, Communications Loss | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
0xxxx | 5616 | 5616 | 01,02 | Event Enable,Subscription Default Active | 1 | 1 | 0.125 |  | 0 = disable, 1 = enable* | RD/CW |  |  | x
| 5651 |  |  | Global Alarm Enable
0xxxx | 5651 | 5651 | 01,02 | Alarm Enable, Not Used | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5652 | 5652 | 01,02 | Alarm Enable, Input Object | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5653 | 5653 | 01,02 | Alarm Enable, Zone Object | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5654 | 5654 | 01,02 | Alarm Enable, ZoneOverride Object | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5655 | 5655 | 01,02 | Alarm Enable, Configuration Mode | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5656 | 5656 | 01,02 | Alarm Enable, Firmware Download | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5657 | 5657 | 01,02 | Alarm Enable, Special Day Object | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5658 | 5658 | 01,02 | Alarm Enable, Schedule Object | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5659 | 5659 | 01,02 | Alarm Enable, Direct Breaker Control Object | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5660 | 5660 | 01,02 | Alarm Enable, Learn Mode | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5661 | 5661 | 01,02 | Alarm Enable, Reset | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5662 | 5662 | 01,02 | Alarm Enable, Bus Present | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5663 | 5663 | 01,02 | Alarm Enable, Breaker Present | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5664 | 5664 | 01,02 | Alarm Enable, Remote Source Objects | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5665 | 5665 | 01,02 | Alarm Enable, Communications Loss | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
0xxxx | 5666 | 5666 | 01,02 | Alarm Enable,Subscription Default Active | 1 | 1 | 0.125 |  | 0 = disable*, 1 = enable | RD/CW |  |  | x
| 6001 |  |  | Breaker Control Manual
0xxxx | 6001 | 6032 | 01,02 | Direct Breaker Control State Manual, Bus Address A | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6033 | 6064 | 01,02 | Direct Breaker Control State Manual, Bus Address B | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6065 | 6096 | 01,02 | Direct Breaker Control State Manual, Bus Address C | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6097 | 6128 | 01,02 | Direct Breaker Control State Manual, Bus Address D | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6129 | 6160 | 01,02 | Direct Breaker Control State Manual, Bus Address E | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6161 | 6192 | 01,02 | Direct Breaker Control State Manual, Bus Address F | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6193 | 6224 | 01,02 | Direct Breaker Control State Manual, Bus Address G | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6225 | 6256 | 01,02 | Direct Breaker Control State Manual, Bus Address H | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6257 | 6288 | 01,02 | Direct Breaker Control State Manual, Bus Address I | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6289 | 6320 | 01,02 | Direct Breaker Control State Manual, Bus Address J | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6321 | 6352 | 01,02 | Direct Breaker Control State Manual, Bus Address K | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6353 | 6384 | 01,02 | Direct Breaker Control State Manual, Bus Address L | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6385 | 6416 | 01,02 | Direct Breaker Control State Manual, Bus Address M | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6417 | 6448 | 01,02 | Direct Breaker Control State Manual, Bus Address N | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6449 | 6480 | 01,02 | Direct Breaker Control State Manual, Bus Address O | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6481 | 6512 | 01,02 | Direct Breaker Control State Manual, Bus Address P | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
| 6601 |  |  | Breaker Control Auto
0xxxx | 6601 | 6632 | 01,02 | Direct Breaker Control State Auto, Bus Address A | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6633 | 6664 | 01,02 | Direct Breaker Control State Auto, Bus Address B | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6665 | 6696 | 01,02 | Direct Breaker Control State Auto, Bus Address C | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6697 | 6728 | 01,02 | Direct Breaker Control State Auto, Bus Address D | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6729 | 6760 | 01,02 | Direct Breaker Control State Auto, Bus Address E | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6761 | 6792 | 01,02 | Direct Breaker Control State Auto, Bus Address F | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6793 | 6824 | 01,02 | Direct Breaker Control State Auto, Bus Address G | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6825 | 6856 | 01,02 | Direct Breaker Control State Auto, Bus Address H | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6857 | 6888 | 01,02 | Direct Breaker Control State Auto, Bus Address I | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6889 | 6920 | 01,02 | Direct Breaker Control State Auto, Bus Address J | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6921 | 6952 | 01,02 | Direct Breaker Control State Auto, Bus Address K | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6953 | 6984 | 01,02 | Direct Breaker Control State Auto, Bus Address L | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 6985 | 7016 | 01,02 | Direct Breaker Control State Auto, Bus Address M | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 7017 | 7048 | 01,02 | Direct Breaker Control State Auto, Bus Address N | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 7049 | 7080 | 01,02 | Direct Breaker Control State Auto, Bus Address O | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
0xxxx | 7081 | 7112 | 01,02 | Direct Breaker Control State Auto, Bus Address P | 32 | 1 | 4 |  | 0 = OFF*, 1 = ON | RD/WR |  |  | x
| 7501 |  |  | Schedule Defined Control
0xxxx | 7501 | 7564 | 01 | Schedule Defined Control ,Schedule 1 - 64 | 64 | 1 | 8 |  | 0 = undefined, 1 = defined* | RD/CW |  |  | x
| 7601 |  |  | Schedule Active Control
0xxxx | 7601 | 7664 | 01 | Schedule Active Control , Schedule 1 - 64 | 64 | 1 | 8 |  | 0 = inactive, 1 = active* | RD/CW |  |  | x
| 8801 |  |  | Period Defined Control
0xxxx | 7701 | 8724 | 01 | Period Defined Control ,Schedule 1 - 1024 | 1024 | 1 | 128 |  | 0 = undefined, 1 = defined* | RD/CW |  |  | x
| 8801 |  |  | Period Active Control
0xxxx | 8801 | 9824 | 01 | Period Active Control ,Schedule 1 - 1024 | 1024 | 1 | 128 |  | 0 = inactive, 1 = active* | RD/CW |  |  | x
| 10101 |  |  | Special Day Defined Control
0xxxx | 10001 | 10096 | 01 | Special Day Defined Control ,Schedule 1 - 96 | 96 | 1 | 12 |  | 0 = undefined, 1 = defined* | RD/CW |  |  | x
| 10101 |  |  | Special Day Active Control
0xxxx | 10101 | 10196 | 01 | Special Day Active Control ,Schedule 1 - 96 | 96 | 1 | 12 |  | 0 = inactive, 1 = active* | RD/CW |  |  | x
| 10201 |  |  | Cbus Output Defined Configuration
0xxxx | 10201 | 10456 | 01,02 | Cbus Output Defined Control , Output 1 - 256 | 256 | 1 | 32 |  | 0 = undefined, 1 = defined* | RD/CW |  |  | x
| 10501 |  |  | Cbus Output Active Configuration
0xxxx | 10501 | 10756 | 01,02 | Cbus Output Active Control , Output 1 - 256 | 256 | 1 | 32 |  | 0 = inactive, 1 = active* | RD/CW |  |  | x
1xxxx "Discrete Input" (Bit)
| 20001 |  |  | Terminal Status
1xxxx | 20001 | 20016 | 01,02 | Terminal State, Terminals 1-16 | 16 | 1 | 32 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 20021 |  |  | Terminal Switch Status
1xxxx | 20021 | 20036 | 01,02 | Terminal Switch State Terminals 1-16 | 16 | 1 | 32 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 20041 |  |  | Terminal Binary Status
1xxxx | 20041 | 20056 | 01,02 | Terminal Binary Activity, Terminals 1-16 | 16 | 1 | 32 |  | 0 = InActive*, 1 = Active | RO |  |  | x
| 20061 |  |  | Terminal Output Status
1xxxx | 20061 | 20076 | 01,02 | Terminal Output Status, Terminals 1-16 | 16 | 1 | 32 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 20081 |  |  | Terminal Level Active Status
1xxxx | 20081 | 20096 | 01,02 | Terminal Level Activity, Terminals 1-16 | 16 | 1 | 32 |  | 0 = InActive*, 1 = Active | RO |  |  | x
| 20101 |  |  | Terminal A/D Error Status
1xxxx | 20101 | 20116 | 01,02 | Terminal A/D Range Error, Terminals 1-16 | 16 | 1 | 32 |  | 0 = no Error*, 1 = Error | RO |  |  | x
| 20201 |  |  | Input Object Status
1xxxx | 20201 | 20456 | 01,02 | Input Object State, Inputs 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 20501 |  |  | Input - Terminal Inhibit Status
1xxxx | 20501 | 20756 | 01,02 | Input Inhibit State, Inputs 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 20801 |  |  | Input Timer Inhibit Status
1xxxx | 20801 | 21056 | 01,02 | Input Timer Inhibit State, Inputs 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 21801 |  |  | Input Manual Flag Status
1xxxx | 21801 | 22056 | 01,02 | Input Object Manual Flag, Inputs 1 - 256 | 256 | 1 | 32 |  | 0 = auto*, 1 = manual | RO |  |  | x
| 22101 |  |  | Zone Object Status
1xxxx | 22101 | 22356 | 01,02 | Zone Object State, Zones 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 22401 |  |  | Zone Manual Flag Status
1xxxx | 22401 | 22656 | 01,02 | Zone Manual Flag, Zones 1 - 256 | 256 | 1 | 32 |  | 0 = auto*, 1 = manual | RO |  |  | x
| 22701 |  |  | Zone Actual Status
1xxxx | 22701 | 22956 | 01,02 | Zone Actual State, Zones 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 23001 |  |  | Zone Event Status
1xxxx | 23001 | 23256 | 01,02 | Zone Event State, Zones 1 - 256 | 256 | 1 | 32 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 23301 |  |  | Zone Alarm Status
1xxxx | 23301 | 23556 | 01,02 | Alarm Status, Zone Object State, Zone 1 - 256 | 256 | 1 | 32 |  | 0 = Normal*, 1 = In alarm | RO |  |  | x
| 24001 |  |  | Schedule Status
1xxxx | 24001 | 24064 | 01,02 | Schedule Output Status, 1 - 64 | 64 | 1 | 8 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 24101 |  |  | Schedule Auto/Manual Status
1xxxx | 24101 | 24164 | 01,02 | Schedule Auto/Manual Output Status, 1 - 64 | 64 | 1 | 8 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 24201 |  |  | Special Day Status
1xxxx | 24201 | 24296 | 01,02 | Special Day Status, 1 - 96 | 96 | 1 | 12 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 24301 |  |  | Special Day Priority Status
1xxxx | 24301 | 24396 | 01,02 | Special Day Status Priority 1, 1 - 96 | 96 | 1 | 12 |  | 0 = OFF*, 1 = ON | RO |  |  | x
1xxxx | 24397 | 24492 | 01,02 | Special Day Status Priority 2, 1 - 96 | 96 | 1 | 12 |  | 0 = OFF*, 1 = ON | RO |  |  | x
1xxxx | 24493 | 24588 | 01,02 | Special Day Status Priority 3, 1 - 96 | 96 | 1 | 12 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 26301 |  |  | Bus Status
1xxxx | 26301 | 26316 | 01,02 | Bus Present, Bus Address A-15 | 1 | 1 | 0.125 |  | 0 = not present, 1 = present | RO |  |  | x
| 26321 |  |  | Bus Non-Responding Status
1xxxx | 26321 | 26336 | 01,02 | Bus Non-Responding | 16 | 1 | 0.125 |  | 0 = responding, 1 = not responding | RO |  |  | x
| 26341 |  |  | Breaker Non-Responding Any Status
1xxxx | 26341 | 26341 | 01,02 | Breaker Non-Responding, Any | 1 | 1 | 0.125 |  | 0 = responding, 1 = not responding | RO |  |  | x
| 26351 |  |  | Non-Responding Zone Status
1xxxx | 26351 | 26606 | 01,02 | Zone Non-Responding | 256 | 1 | 32 |  | 0 = responding, 1 = not responding | RO |  |  | x
| 26611 |  |  | Panel Non-Responding Status
1xxxx | 26611 | 26626 | 01,02 | Panel Non-responding | 16 | 1 | 2 |  | 0 = inactive, 1 = active | RO |  |  | x
| 26701 |  |  | Breaker Actual State Status
1xxxx | 26701 | 26732 | 01,02 | Breaker Actual State, Bus Address A | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 26733 | 26764 | 01,02 | Breaker Actual State, Bus Address B | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 26765 | 26796 | 01,02 | Breaker Actual State, Bus Address C | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 26797 | 26828 | 01,02 | Breaker Actual State, Bus Address D | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 26829 | 26860 | 01,02 | Breaker Actual State, Bus Address E | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 26861 | 26892 | 01,02 | Breaker Actual State, Bus Address F | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 26893 | 26924 | 01,02 | Breaker Actual State, Bus Address G | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 26925 | 26956 | 01,02 | Breaker Actual State, Bus Address H | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 26957 | 26988 | 01,02 | Breaker Actual State, Bus Address I | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 26989 | 27020 | 01,02 | Breaker Actual State, Bus Address J | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27021 | 27052 | 01,02 | Breaker Actual State, Bus Address K | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27053 | 27084 | 01,02 | Breaker Actual State, Bus Address L | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27085 | 27116 | 01,02 | Breaker Actual State, Bus Address M | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27117 | 27148 | 01,02 | Breaker Actual State, Bus Address N | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27149 | 27180 | 01,02 | Breaker Actual State, Bus Address O | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27181 | 27212 | 01,02 | Breaker Actual State, Bus Address P | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
| 27301 |  |  | Breaker Control State Status
1xxxx | 27301 | 27332 | 01,02 | Breaker Control State, Bus Address A | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27333 | 27364 | 01,02 | Breaker Control State, Bus Address B | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27365 | 27396 | 01,02 | Breaker Control State, Bus Address C | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27397 | 27428 | 01,02 | Breaker Control State, Bus Address D | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27429 | 27460 | 01,02 | Breaker Control State, Bus Address E | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27461 | 27492 | 01,02 | Breaker Control State, Bus Address F | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27493 | 27524 | 01,02 | Breaker Control State, Bus Address G | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27525 | 27556 | 01,02 | Breaker Control State, Bus Address H | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27557 | 27588 | 01,02 | Breaker Control State, Bus Address I | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27589 | 27620 | 01,02 | Breaker Control State, Bus Address J | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27621 | 27652 | 01,02 | Breaker Control State, Bus Address K | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27653 | 27684 | 01,02 | Breaker Control State, Bus Address L | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27685 | 27716 | 01,02 | Breaker Control State, Bus Address M | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27717 | 27748 | 01,02 | Breaker Control State, Bus Address N | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27749 | 27780 | 01,02 | Breaker Control State, Bus Address O | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27781 | 27812 | 01,02 | Breaker Control State, Bus Address P | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
| 27901 |  |  | Breaker Intended State Status
1xxxx | 27901 | 27932 | 01,02 | Breaker Intended State, Bus Address A | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27933 | 27964 | 01,02 | Breaker Intended State, Bus Address B | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27965 | 27996 | 01,02 | Breaker Intended State, Bus Address C | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 27997 | 28028 | 01,02 | Breaker Intended State, Bus Address D | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 28029 | 28060 | 01,02 | Breaker Intended State, Bus Address E | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 28061 | 28092 | 01,02 | Breaker Intended State, Bus Address F | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 28093 | 28124 | 01,02 | Breaker Intended State, Bus Address G | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 28125 | 28156 | 01,02 | Breaker Intended State, Bus Address H | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 28157 | 28188 | 01,02 | Breaker Intended State, Bus Address I | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 28189 | 28220 | 01,02 | Breaker Intended State, Bus Address J | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 28221 | 28252 | 01,02 | Breaker Intended State, Bus Address K | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 28253 | 28284 | 01,02 | Breaker Intended State, Bus Address L | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 28285 | 28316 | 01,02 | Breaker Intended State, Bus Address M | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 28317 | 28348 | 01,02 | Breaker Intended State, Bus Address N | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 28349 | 28380 | 01,02 | Breaker Intended State, Bus Address O | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 28381 | 28412 | 01,02 | Breaker Intended State, Bus Address P | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
| 28501 |  |  | Breaker Desired/Direct State Status
1xxxx | 28501 | 28532 | 01,02 | Breaker Desired/Direct State, Bus Address A | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28533 | 28564 | 01,02 | Breaker Desired/Direct State, Bus Address B | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28565 | 28596 | 01,02 | Breaker Desired/Direct State, Bus Address C | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28597 | 28628 | 01,02 | Breaker Desired/Direct State, Bus Address D | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28629 | 28660 | 01,02 | Breaker Desired/Direct State, Bus Address E | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28661 | 28692 | 01,02 | Breaker Desired/Direct State, Bus Address F | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28693 | 28724 | 01,02 | Breaker Desired/Direct State, Bus Address G | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28725 | 28756 | 01,02 | Breaker Desired/Direct State, Bus Address H | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28757 | 28788 | 01,02 | Breaker Desired/Direct State, Bus Address I | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28789 | 28820 | 01,02 | Breaker Desired/Direct State, Bus Address J | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28821 | 28852 | 01,02 | Breaker Desired/Direct State, Bus Address K | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28853 | 28884 | 01,02 | Breaker Desired/Direct State, Bus Address L | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28885 | 28916 | 01,02 | Breaker Desired/Direct State, Bus Address M | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28917 | 28948 | 01,02 | Breaker Desired/Direct State, Bus Address N | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28949 | 28980 | 01,02 | Breaker Desired/Direct State, Bus Address O | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
1xxxx | 28981 | 29012 | 01,02 | Breaker Desired/Direct State, Bus Address P | 32 | 1 | 4 |  | 0 = desired state, 1 = direct control | RO |  |  | x
| 29101 |  |  | Breaker Desired State Status
1xxxx | 29101 | 29132 | 01,02 | Breaker Desired State, Bus Address A | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29133 | 29164 | 01,02 | Breaker Desired State, Bus Address B | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29165 | 29196 | 01,02 | Breaker Desired State, Bus Address C | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29197 | 29228 | 01,02 | Breaker Desired State, Bus Address D | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29229 | 29260 | 01,02 | Breaker Desired State, Bus Address E | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29261 | 29292 | 01,02 | Breaker Desired State, Bus Address F | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29293 | 29324 | 01,02 | Breaker Desired State, Bus Address G | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29325 | 29356 | 01,02 | Breaker Desired State, Bus Address H | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29357 | 29388 | 01,02 | Breaker Desired State, Bus Address I | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29389 | 29420 | 01,02 | Breaker Desired State, Bus Address J | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29421 | 29452 | 01,02 | Breaker Desired State, Bus Address K | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29453 | 29484 | 01,02 | Breaker Desired State, Bus Address L | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29485 | 29516 | 01,02 | Breaker Desired State, Bus Address M | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29517 | 29548 | 01,02 | Breaker Desired State, Bus Address N | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29549 | 29580 | 01,02 | Breaker Desired State, Bus Address O | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
1xxxx | 29581 | 29612 | 01,02 | Breaker Desired State, Bus Address P | 32 | 1 | 4 |  | 0 = OFF, 1 = ON | RO |  |  | x
| 29701 |  |  | Breaker Present Status
1xxxx | 29701 | 29732 | 01,02 | Breaker Present, Bus Address A | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 29733 | 29764 | 01,02 | Breaker Present, Bus Address B | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 29765 | 29796 | 01,02 | Breaker Present, Bus Address C | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 29797 | 29828 | 01,02 | Breaker Present, Bus Address D | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 29829 | 29860 | 01,02 | Breaker Present, Bus Address E | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 29861 | 29892 | 01,02 | Breaker Present, Bus Address F | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 29893 | 29924 | 01,02 | Breaker Present, Bus Address G | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 29925 | 29956 | 01,02 | Breaker Present, Bus Address H | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 29957 | 29988 | 01,02 | Breaker Present, Bus Address I | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 29989 | 30020 | 01,02 | Breaker Present, Bus Address J | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 30021 | 30052 | 01,02 | Breaker Present, Bus Address K | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 30053 | 30084 | 01,02 | Breaker Present, Bus Address L | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 30085 | 30116 | 01,02 | Breaker Present, Bus Address M | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 30117 | 30148 | 01,02 | Breaker Present, Bus Address N | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 30149 | 30180 | 01,02 | Breaker Present, Bus Address O | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
1xxxx | 30181 | 30212 | 01,02 | Breaker Present, Bus Address P | 32 | 1 | 4 |  | 0 = not present, 1 = present | RO |  |  | x
| 30301 |  |  | Breaker Non-Responding Status
1xxxx | 30301 | 30332 | 01,02 | Breaker Non-Responding, Bus Address A | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30333 | 30364 | 01,02 | Breaker Non-Responding, Bus Address B | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30365 | 30396 | 01,02 | Breaker Non-Responding, Bus Address C | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30397 | 30428 | 01,02 | Breaker Non-Responding, Bus Address D | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30429 | 30460 | 01,02 | Breaker Non-Responding, Bus Address E | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30461 | 30492 | 01,02 | Breaker Non-Responding, Bus Address F | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30493 | 30524 | 01,02 | Breaker Non-Responding, Bus Address G | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30525 | 30556 | 01,02 | Breaker Non-Responding, Bus Address H | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30557 | 30588 | 01,02 | Breaker Non-Responding, Bus Address I | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30589 | 30620 | 01,02 | Breaker Non-Responding, Bus Address J | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30621 | 30652 | 01,02 | Breaker Non-Responding, Bus Address K | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30653 | 30684 | 01,02 | Breaker Non-Responding, Bus Address L | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30685 | 30716 | 01,02 | Breaker Non-Responding, Bus Address M | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30717 | 30748 | 01,02 | Breaker Non-Responding, Bus Address N | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30749 | 30780 | 01,02 | Breaker Non-Responding, Bus Address O | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
1xxxx | 30781 | 30812 | 01,02 | Breaker Non-Responding, Bus Address P | 32 | 1 | 4 |  | 0 = responding, 1 = not responding | RO |  |  | x
| 31001 |  |  | Subscriber State
1xxxx | 31001 | 31064 | 01,02 | Subscriber State | 64 | 1 | 8 |  | 0 = inactive, 1 = active | RO |  |  | x
| 31201 |  |  | Remote Source Status
1xxxx | 31201 | 31264 | 01,02 | Remote Source Status | 64 | 1 | 8 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 31401 |  |  | Remote Source Auto Status
1xxxx | 31401 | 31528 | 01,02 | Remote Source Auto Status | 128 | 1 | 16 |  | 0 = Auto 1 = Manaul | RO |  |  | x
| 31601 |  |  | Subscriber Default Active Status
1xxxx | 31601 | 31728 | 01,02 | Subscriber Default Active | 128 | 1 | 16 |  | 0 = OFF*, 1 = ON | RO |  |  | x
| 31801 |  |  | Publisher State
1xxxx | 31801 | 32312 | 01,02 | Publisher State | 512 | 1 | 64 |  | 0 = inactive, 1 = active | RO |  |  | x
|  |  |  | Total Coils per Reference Type | 6690 | 132 | 834.375
|  |  |  | Total Coils | 6690 |  | 834.375
Invalid Registers will return a value of 0x8000
Status Registers
3xxxx "Input Registers" (2 Byte)
| 1 |  |  | Bus Model Status
3xxxx | 1 | 16 | 03,04 | Bus Model, Bus 1-16 | 16 | 1 | 32 | 16 | Bus Model Number | RO |  |  | x
| 17 |  |  | Bus Firmware Status
3xxxx | 17 | 32 | 03,04 | Bus Firmware Version, Bus 1-16 | 16 | 1 | 32 | 16 | Firmware Version | RO |  |  | x
| 33 |  |  | Breaker Blink Timer Status
3xxxx | 33 | 56 | 03,04 | Breaker Blink Timer Value, Bus Address A | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 57 | 80 | 03,04 | Breaker Blink Timer Value, Bus Address B | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 81 | 104 | 03,04 | Breaker Blink Timer Value, Bus Address C | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 105 | 128 | 03,04 | Breaker Blink Timer Value, Bus Address D | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 129 | 152 | 03,04 | Breaker Blink Timer Value, Bus Address E | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 153 | 176 | 03,04 | Breaker Blink Timer Value, Bus Address F | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 177 | 200 | 03,04 | Breaker Blink Timer Value, Bus Address G | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 201 | 224 | 03,04 | Breaker Blink Timer Value, Bus Address H | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 225 | 248 | 03,04 | Breaker Blink Timer Value, Bus Address I | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 249 | 272 | 03,04 | Breaker Blink Timer Value, Bus Address J | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 273 | 296 | 03,04 | Breaker Blink Timer Value, Bus Address K | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 297 | 320 | 03,04 | Breaker Blink Timer Value, Bus Address L | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 321 | 344 | 03,04 | Breaker Blink Timer Value, Bus Address M | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 345 | 368 | 03,04 | Breaker Blink Timer Value, Bus Address N | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 369 | 392 | 03,04 | Breaker Blink Timer Value, Bus Address O | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
3xxxx | 393 | 416 | 03,04 | Breaker Blink Timer Value, Bus Address P | 24 | 1 | 48 | 24 | time, s, remaining | RO |  |  | x
| 417 |  |  | Breaker Type
3xxxx | 417 | 440 | 03,04 | Breaker Type, Bus Address A | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 441 | 464 | 03,04 | Breaker Type, Bus Address B | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 465 | 488 | 03,04 | Breaker Type, Bus Address C | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 489 | 512 | 03,04 | Breaker Type, Bus Address D | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 513 | 536 | 03,04 | Breaker Type, Bus Address E | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 537 | 560 | 03,04 | Breaker Type, Bus Address F | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 561 | 584 | 03,04 | Breaker Type, Bus Address G | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 585 | 608 | 03,04 | Breaker Type, Bus Address H | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 609 | 632 | 03,04 | Breaker Type, Bus Address I | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 633 | 656 | 03,04 | Breaker Type, Bus Address J | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 657 | 680 | 03,04 | Breaker Type, Bus Address K | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 681 | 704 | 03,04 | Breaker Type, Bus Address L | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 705 | 728 | 03,04 | Breaker Type, Bus Address M | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 729 | 752 | 03,04 | Breaker Type, Bus Address N | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 753 | 776 | 03,04 | Breaker Type, Bus Address O | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
3xxxx | 777 | 800 | 03,04 | Breaker Type, Bus Address P | 24 | 1 | 48 | 24 | breaker types | RO |  |  | x
| 2401 |  |  | Clock/Calendar Status
3xxxx | 2401 | 2401 | 03,04 | Daylight Saving Time Active | 1 | 1 | 2 | 1 | 0=inactive*, 1=active | RO |  |  | x
3xxxx | 2402 | 2402 | 03,04 | Calculated Day of the Week | 1 | 1 | 2 | 1 | day of week | RO |  |  | x
3xxxx | 2403 | 2403 | 03,04 | Calculated Week of the Month | 1 | 1 | 2 | 1 | week of month | RO |  |  | x
3xxxx | 2404 | 2404 | 03,04 | Calculated DST Begin Month | 1 | 1 | 2 | 1 | month | RO |  |  | x
3xxxx | 2405 | 2405 | 03,04 | Calculated DST Begin Day | 1 | 1 | 2 | 1 | day | RO |  |  | x
3xxxx | 2406 | 2406 | 03,04 | Calculated DST End Month | 1 | 1 | 2 | 1 | month | RO |  |  | x
3xxxx | 2407 | 2407 | 03,04 | Calculated DST End Day | 1 | 1 | 2 | 1 | day | RO |  |  | x
3xxxx | 2408 | 2408 | 03,04 | Calculated Sunrise Time, Hour | 1 | 1 | 2 | 1 | sunrise time | RO |  |  | x
3xxxx | 2409 | 2409 | 03,04 | Calculated Sunrise Time, Minutes | 1 | 1 | 2 | 1 | sunrise time | RO |  |  | x
3xxxx | 2410 | 2410 | 03,04 | Calculated Sunset Time, Hour | 1 | 1 | 2 | 1 | sunset time | RO |  |  | x
3xxxx | 2411 | 2411 | 03,04 | Calculated Sunset Time, Minutes | 1 | 1 | 2 | 1 | sunset time | RO |  |  | x
0
3xxxx
3xxxx
3xxxx
3xxxx
3xxxx
3xxxx
3xxxx
3xxxx
3xxxx
3xxxx
3xxxx
3xxxx
3xxxx
3xxxx
3xxxx
| 3001 |  |  | Modbus Communications Status
3xxxx | 3001 | 3001 | 03,04 | No. of Modbus messages rx this unit | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3002 | 3002 | 03,04 | No. of Modbus messages tx this units | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3003 | 3003 | 03,04 | No. of Modbus messages with valid CRC | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3004 | 3004 | 03,04 | No. of Modbus messages with valid LRC | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3005 | 3005 | 03,04 | No. of Modbus broadcast messages | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3006 | 3006 | 03,04 | No. of Modbus messages with invalid CRC | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3007 | 3007 | 03,04 | No. of Modbus messages with invalid LRC | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3008 | 3008 | 03,04 | No. of Messages with illegal opcode/function code | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3009 | 3009 | 03,04 | No. of Messages with exceptions | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3010 | 3010 | 03,04 | Modbus Event Counter | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3011 | 3011 | 03,04 | No. of Messages with illegal count | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3012 | 3012 | 03,04 | No. of Messages with frame error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3013 | 3013 | 03,04 | No. of Messages to other devices | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
| 3021 |  |  | Ethernet Communications Status
3xxxx | 3021 | 3021 | 03,04 | Ethernet Port Link Bitmap | 1 | 1 | 2 | 1 | bit 0-port1,bit 1-port2,bit 2-port3, 0=no link, 1=link | RO |  |  | x
3xxxx | 3022 | 3022 | 03,04 | Free Ethernet stack buffers | 1 | 1 | 2 | 1 | 0-256 | RO |  |  | x
3xxxx | 3023 | 3023 | 03,04 | Ethernet rx frames | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3024 | 3024 | 03,04 | Ethernet tx frames | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3025 | 3025 | 03,04 | Ethernet rx frames with errors | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3026 | 3026 | 03,04 | Ethernet tx frames with errors | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3027 | 3027 | 03,04 | TCP frames rx | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3028 | 3028 | 03,04 | TCP frames tx | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3029 | 3029 | 03,04 | TCP frame errors | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3030 | 3030 | 03,04 | ICMP frames transmitted | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3031 | 3031 | 03,04 | ICMP frames received | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3032 | 3032 | 03,04 | UDP frames rx | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3033 | 3033 | 03,04 | UDP frames tx | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3034 | 3034 | 03,04 | UDP frames errors | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3035 | 3035 | 03,04 | ARP frames rx | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3036 | 3036 | 03,04 | ARP frames tx | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3037 | 3037 | 03,04 | IP frame errors | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3038 | 3038 | 03,04 | IP frames discarded | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3039 | 3039 | 03,04 | IP last error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3040 | 3040 | 03,04 | Ethernet Interrupts | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3041 | 3041 | 03,04 | Unknown frames rx | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3042 | 3042 | 03,04 | PPP rx frame errors | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3043 | 3043 | 03,04 | Fragmented rx frames | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3044 | 3044 | 03,04 | Ethernet errhw | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
| 3045 | 3045 | 03,04 | Ethernet errlw | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3046 |  |  | Ethernet Modbus Connection Status
3xxxx | 3046 | 3046 | 03,04 | Modbus Connection Bitmap | 1 | 1 | 2 | 1 | 0=not connected, 1=connected: bit 0-connection 1,bit 1-connection 2,....bit 15-connection 16 | RO |  |  | x
3xxxx | 3047 | 3062 | 03,04 | Connection Time-Out Counter | 16 | 1 | 32 | 16 | 0 - 65535 seconds, increments when connection lost | RO |  |  | x
3xxxx | 3063 | 3094 | 03,04 | Modbus Connection SessionTimer | 32 | 1 | 64 | 32 | 0 - 2^32 seconds, connection session timer | RO |  |  | x
3xxxx | 3101 |  |  | RS232 Serial Communications Status
3xxxx | 3101 | 3101 | 03,04 | Uart 2 Rx Break Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3102 | 3102 | 03,04 | Uart 2 Rx Frame Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3103 | 3103 | 03,04 | Uart 2 Rx Parity Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3104 | 3104 | 03,04 | Uart 2 Rx Overrun Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3105 | 3105 | 03,04 | Modbus RTU Overrun | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3106 | 3106 | 03,04 | Modbus Ascii Overrun | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3107 | 3107 | 03,04 | Rx Queue Pending Timeout | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3108 | 3108 | 03,04 | Modbus Pass-through Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
| 3109 | 3109 | 03,04 | Modbus Ascii Timeout | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3110 |  |  | RS485 Serial Communications Status
3xxxx | 3110 | 3110 | 03,04 | Uart 1 Rx Break Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3111 | 3111 | 03,04 | Uart 1 Rx Frame Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3112 | 3112 | 03,04 | Uart 1 Rx Parity Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3113 | 3113 | 03,04 | Uart 1 Rx Overrun Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3114 | 3114 | 03,04 | Modbus RTU Overrun | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3115 | 3115 | 03,04 | Modbus Ascii Overrun | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3116 | 3116 | 03,04 | Rx Queue Pending Timeout | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3117 | 3117 | 03,04 | Modbus Pass-through Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
| 3118 | 3118 | 03,04 | Modbus Ascii Timeout | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3119 |  |  | RS485 Serial Smartbus Communications Status
3xxxx | 3119 | 3119 | 03,04 | Uart 0 Rx Break Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3120 | 3120 | 03,04 | Uart 0 Rx Frame Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3121 | 3121 | 03,04 | Uart 0 Rx Parity Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3122 | 3122 | 03,04 | Uart 0 Rx Overrun Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3123 | 3123 | 03,04 | Modbus RTU Overrun | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3124 | 3124 | 03,04 | Modbus Ascii Overrun | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3125 | 3125 | 03,04 | Fifo Timeout | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3126 | 3126 | 03,04 | Tx Reply Timeout | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3127 | 3127 | 03,04 | Pass-through Ethernet Errors | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3128 | 3128 | 03,04 | Breaker Manager Error | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3129 | 3129 | 03,04 | Pass-through Packets | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3130 | 3130 | 03,04 | Breaker Manager Packets | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3131 | 3131 | 03,04 | Total number of messages | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3132 | 3132 | 03,04 | Modbus LRC Errors | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3133 | 3133 | 03,04 | Modbus CRC Errors | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
| 3134 |  |  | Control Bus Communications Status
3xxxx | 3134 | 3134 | 03,04 | No. of Modbus messages sent to bus 0 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3135 | 3135 | 03,04 | No. of Modbus good messages received from bus 0 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3136 | 3136 | 03,04 | No. of Modbus bus timeouts 0 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3137 | 3137 | 03,04 | No. of LRC\CRC errors from bus 0 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3138 | 3138 | 03,04 | No. of exception responses from bus 0 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3139 | 3139 | 03,04 | No. of Modbus messages sent to bus 1 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3140 | 3140 | 03,04 | No. of Modbus good messages received from bus 1 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3141 | 3141 | 03,04 | No. of Modbus bus timeouts 1 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3142 | 3142 | 03,04 | No. of LRC\CRC errors from bus 1 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3143 | 3143 | 03,04 | No. of exception responses from bus 1 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3144 | 3144 | 03,04 | No. of Modbus messages sent to bus 2 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3145 | 3145 | 03,04 | No. of Modbus good messages received from bus 2 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3146 | 3146 | 03,04 | No. of Modbus bus timeouts 2 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3147 | 3147 | 03,04 | No. of LRC\CRC errors from bus 2 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3148 | 3148 | 03,04 | No. of exception responses from bus 2 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3149 | 3149 | 03,04 | No. of Modbus messages sent to bus 3 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3150 | 3150 | 03,04 | No. of Modbus good messages received from bus 3 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3151 | 3151 | 03,04 | No. of Modbus bus timeouts 3 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3152 | 3152 | 03,04 | No. of LRC\CRC errors from bus 3 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3153 | 3153 | 03,04 | No. of exception responses from bus 3 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3154 | 3154 | 03,04 | No. of Modbus messages sent to bus 4 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3155 | 3155 | 03,04 | No. of Modbus good messages received from bus 4 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3156 | 3156 | 03,04 | No. of Modbus bus timeouts 4 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3157 | 3157 | 03,04 | No. of LRC\CRC errors from bus 4 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3158 | 3158 | 03,04 | No. of exception responses from bus 4 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3159 | 3159 | 03,04 | No. of Modbus messages sent to bus 5 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3160 | 3160 | 03,04 | No. of Modbus good messages received from bus 5 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3161 | 3161 | 03,04 | No. of Modbus bus timeouts 5 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3162 | 3162 | 03,04 | No. of LRC\CRC errors from bus 5 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3163 | 3163 | 03,04 | No. of exception responses from bus 5 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3164 | 3164 | 03,04 | No. of Modbus messages sent to bus 6 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3165 | 3165 | 03,04 | No. of Modbus good messages received from bus 6 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3166 | 3166 | 03,04 | No. of Modbus bus timeouts 6 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3167 | 3167 | 03,04 | No. of LRC\CRC errors from bus 6 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3168 | 3168 | 03,04 | No. of exception responses from bus 6 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3169 | 3169 | 03,04 | No. of Modbus messages sent to bus 7 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3170 | 3170 | 03,04 | No. of Modbus good messages received from bus 7 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3171 | 3171 | 03,04 | No. of Modbus bus timeouts 7 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3172 | 3172 | 03,04 | No. of LRC\CRC errors from bus 7 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3173 | 3173 | 03,04 | No. of exception responses from bus 7 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3174 | 3174 | 03,04 | No. of Modbus messages sent to bus 8 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3175 | 3175 | 03,04 | No. of Modbus good messages received from bus 8 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3176 | 3176 | 03,04 | No. of Modbus bus timeouts 8 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3177 | 3177 | 03,04 | No. of LRC\CRC errors from bus 8 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3178 | 3178 | 03,04 | No. of exception responses from bus 8 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3179 | 3179 | 03,04 | No. of Modbus messages sent to bus 9 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3180 | 3180 | 03,04 | No. of Modbus good messages received from bus 9 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3181 | 3181 | 03,04 | No. of Modbus bus timeouts 9 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3182 | 3182 | 03,04 | No. of LRC\CRC errors from bus 9 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3183 | 3183 | 03,04 | No. of exception responses from bus 9 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3184 | 3184 | 03,04 | No. of Modbus messages sent to bus 10 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3185 | 3185 | 03,04 | No. of Modbus good messages received from bus 10 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3186 | 3186 | 03,04 | No. of Modbus bus timeouts 10 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3187 | 3187 | 03,04 | No. of LRC\CRC errors from bus 10 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3188 | 3188 | 03,04 | No. of exception responses from bus 10 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3189 | 3189 | 03,04 | No. of Modbus messages sent to bus 11 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3190 | 3190 | 03,04 | No. of Modbus good messages received from bus 11 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3191 | 3191 | 03,04 | No. of Modbus bus timeouts 11 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3192 | 3192 | 03,04 | No. of LRC\CRC errors from bus 11 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3193 | 3193 | 03,04 | No. of exception responses from bus 11 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3194 | 3194 | 03,04 | No. of Modbus messages sent to bus 12 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3195 | 3195 | 03,04 | No. of Modbus good messages received from bus 12 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3196 | 3196 | 03,04 | No. of Modbus bus timeouts 12 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3197 | 3197 | 03,04 | No. of LRC\CRC errors from bus 12 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3198 | 3198 | 03,04 | No. of exception responses from bus 12 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3199 | 3199 | 03,04 | No. of Modbus messages sent to bus 13 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3200 | 3200 | 03,04 | No. of Modbus good messages received from bus 13 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3201 | 3201 | 03,04 | No. of Modbus bus timeouts 13 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3202 | 3202 | 03,04 | No. of LRC\CRC errors from bus 13 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3203 | 3203 | 03,04 | No. of exception responses from bus 13 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3204 | 3204 | 03,04 | No. of Modbus messages sent to bus 14 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3205 | 3205 | 03,04 | No. of Modbus good messages received from bus 14 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3206 | 3206 | 03,04 | No. of Modbus bus timeouts 14 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3207 | 3207 | 03,04 | No. of LRC\CRC errors from bus 14 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3208 | 3208 | 03,04 | No. of exception responses from bus 14 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3209 | 3209 | 03,04 | No. of Modbus messages sent to bus 15 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3210 | 3210 | 03,04 | No. of Modbus good messages received from bus 15 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3211 | 3211 | 03,04 | No. of Modbus bus timeouts 15 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3212 | 3212 | 03,04 | No. of LRC\CRC errors from bus 15 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3213 | 3213 | 03,04 | No. of exception responses from bus 15 | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3214 | 3214 | 03,04 | No. of Modbus messages sent (to all busses) | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
3xxxx | 3215 | 3215 | 03,04 | No. of Modbus frame errors received (from all busses) | 1 | 1 | 2 | 1 | 0 - 65535 | RO |  |  | x
| 4001 |  |  | Terminal Status
3xxxx | 4001 | 4016 | 03,04 | Terminal 8-bit Valuel Status, Terminals 1-16 | 16 | 1 | 32 | 16 | 0-255, 8 bit A/D | RO |  |  | x
3xxxx | 4017 | 4032 | 03,04 | Terminal 8- bit Percentage Status, Terminals 1-16 | 16 | 1 | 32 | 16 | 0-100%, 8 bit A/D | RO |  |  | x
3xxxx | 4033 | 4064 | 03,04 | Terminal 8-bit Scaled Status, Terminals 1-16 | 32 | 1 | 64 | 32 | Scaled floating pt value, 8 bit A/D | RO |  |  | x
3xxxx | 4065 | 4080 | 03,04 | Terminal 12 bit Value Status, Terminals 1-16 | 16 | 1 | 32 | 16 | 0-4095, 12 bit A/D | RO |  |  | x
3xxxx | 4081 | 4096 | 03,04 | Terminal 12- bit Percentage Status, Terminals 1-16 | 16 | 1 | 32 | 16 | 0-100%, 12 bit A/D | RO |  |  | x
3xxxx | 4097 | 4128 | 03,04 | Terminal 12-bit Scaled Status, Terminals 1-16 | 32 | 1 | 64 | 32 | Scaled floating pt value, 12 bit A/D | RO |  |  | x
| 4201 |  |  | Input Status
3xxxx | 4201 | 4456 | 03,04 | Input Timer Value, Input 1 - 256 | 256 | 1 | 512 | 256 | 0 - 64800 seconds | RO |  |  | x
3xxxx | 4457 | 4712 | 03,04 | Input Analog Level Value, Input 1 - 256 | 256 | 1 | 512 | 256 | 0 - 255 counts | RO |  |  | x
| 6001 |  |  | Zone Status
3xxxx | 6001 | 6256 | 03,04 | Zone Override Timer Value, Zones 1-256 | 256 | 1 | 512 | 256 | 0-65535 | RO |  |  | x
3xxxx | 6257 | 6512 | 03,04 | Zone Truth Table, Zones 1-256 | 256 | 1 | 512 | 256 | 0-65535 | RO |  |  | x
| 8990 |  |  | Event Log Start & End Record
3xxxx | 8990 | 8990 | 03,04 | Event Log Newest Record | 1 | 1 | 2 | 1 | 0-65535 | RO |  |  | x
3xxxx | 8991 | 8991 | 03,04 | Event Log Oldest Record | 1 | 1 | 2 | 1 | 0-65535 | RO |  |  | x
| 9001 |  |  | CRC Status
3xxxx | 9001 | 9002 | 03,04 | Terminal Object - File 1 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9003 | 9004 | 03,04 | Input Object - File 2 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9005 | 9006 | 03,04 | Panel Object - File 3 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9007 | 9008 | 03,04 | Zone Object - File 4 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9009 | 9010 | 03,04 | Schedule Object - File 5 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9011 | 9012 | 03,04 | Periods Object - File 6 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9013 | 9014 | 03,04 | Special Day Object - File 7 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9015 | 9016 | 03,04 | Bus Object - File 8 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9017 | 9018 | 03,04 | Subscriber Object - File 10 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9019 | 9020 | 03,04 | Cbus Output Object - File 12 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9021 | 9022 | 03,04 | Comms Object - File 15 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9023 | 9024 | 03,04 | System Object - File 14 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9025 | 9026 | 03,04 | Clock Object - File 16 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9027 | 9028 | 03,04 | Terminal Nametag - File 101 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9029 | 9030 | 03,04 | Input Nametag - File 102 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9031 | 9032 | 03,04 | Panel Nametag | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9033 | 9034 | 03,04 | Zone Nametag - File 104 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9035 | 9036 | 03,04 | Schedule Nametag - File 105 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9037 | 9038 | 03,04 | Period Nametag - File 106 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9039 | 9040 | 03,04 | Special Day Nametag - File 107 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9041 | 9042 | 03,04 | Bus Nametag - File 108 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9043 | 9044 | 03,04 | Breaker Nametag - File 118 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9045 | 9046 | 03,04 | PanelPositionNametag - File 119 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9047 | 9048 | 03,04 | Bus/Breaker Hardware Status | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9049 | 9050 | 03,04 | Cbus Output Nametags - File 110 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9051 | 9052 | 03,04 | Publisher Object - File 9 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9053 | 9054 | 03,04 | Subscriber Nametag - File 110 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
3xxxx | 9055 | 9056 | 03,04 | Email Address - File 115 | 2 | 1 | 4 | 2 | 0-2^32 - 32 bit CRC of File | RO |  |  | x
| 9201 |  |  | Cbus Local Network Device Addresses Status
3xxxx | 9201 | 9456 | 03,04 | Cbus Device Addresses, 1-256 | 256 | 1 | 1 | 256 | 0 - 255, 0xFF=not used | RO |  |  | x
| 9501 |  |  | SNTP Update Status
3xxxx | 9501 | 9506 | 03,04 | SNTP Last Successful Update, date/time | 1 | 6 | 12 | 6 | format | RO |  |  | x
3xxxx | 9507 | 9507 | 03,04 | SNTP Last Successful Update, server | 1 | 1 | 2 | 1 | Server 1 = 1, Server 2 = 2 | RO |  |  | x
| 9521 |  |  | Email Error Status
3xxxx | 9521 | 9521 | 03,04 | Email Error Status | 1 | 1 | 2 | 1 | email errors | RO |  |  | x
| 9601 |  |  | Subscriber Timers
3xxxx | 9601 | 9664 | 03,04 | Subscriber Heartbeat | 64 | 1 | 128 | 64 | 0 - 65535 | RO |  |  | x
| 9701 |  |  | Publisher Timers
3xxxx | 9701 | 10212 | 03,04 | Publisher Timeout Count | 512 | 1 | 512 | 512 | 0 - 65535 | RO |  |  | x
| 10301 |  |  | Publisher PeriodicTimers
3xxxx | 10301 | 10812 | 03,04 | Publisher PeriodicTimers | 512 | 1 | 512 | 512 | 0 - 65535 | RO |  |  | x
| 34001 |  |  | System Status
3xxxx | 34001 | 34001 | 03,04 | Boot Firmware Version | 1 | 1 | 2 | 1 | MSByte: version, LSByte: revision- example | RO |  |  | x
3xxxx | 34002 | 34002 | 03,04 | Download Module Firmware Version | 1 | 1 | 2 | 1 | MSByte: version, LSByte: revision | RO |  |  | x
3xxxx | 34003 | 34003 | 03,04 | Control Module Firmware Version | 1 | 1 | 2 | 1 | MSByte: version, LSByte: revision | RO |  |  | x
3xxxx | 34004 | 34004 | 03,04 | Command Interface Password | 1 | 1 | 2 | 1 | random value | RO |  |  | x
3xxxx | 34005 | 34005 | 03,04 | Self-Test Bitmap | 1 | 1 | 2 | 1 | bit-map | RO |  |  | x
3xxxx | 34006 | 34006 | 03,04 | Control Module Model | 1 | 1 | 2 | 1 | 1500 | RO |  |  | x
3xxxx | 34007 | 34007 | 03,04 | Hardware Peripheral Status | 1 | 1 | 2 | 1 | hardware peripheral status | RO |  |  | x
3xxxx | 34008 | 34008 | 03,04 | DLF Compatibility | 1 | 1 | 2 | 1 | DLF compatibility - 101=App running, 100=Download Mode | RO |  |  | x
3xxxx | 34009 | 34009 | 03,04 |  | 1 | 1 | 2 | 1 |  | RO
3xxxx | 34010 | 34010 | 03,04 |  | 1 | 1 | 2 | 1 |  | RO
3xxxx | 34011 | 34011 | 03,04 |  | 1 | 1 | 2 | 1 |  | RO
3xxxx | 34012 | 34012 | 03,04 | Hardware/External Reset Counter | 1 | 1 | 2 | 1 | 0-65535 - hardware watchdog reset - pushbutton & resets | RO |  |  | x
3xxxx | 34013 | 34013 | 03,04 |  | 1 | 1 | 2 | 1 |  | RO
3xxxx | 34014 | 34014 | 03,04 |  | 1 | 1 | 2 | 1 |  | RO
3xxxx | 34015 | 34015 | 03,04 | Database Version | 1 | 1 | 2 | 1 | MSByte: version, LSByte: revision | RO |  |  | x
3xxxx | 34016 | 34016 | 03,04 | Key Press Status | 1 | 1 | 2 | 1 | key press status | RO |  |  | x
3xxxx | 34017 | 34017 | 03,04 | Beta Version | 1 | 1 | 2 | 1 | 0=not Beta firmware, 1= Beta firmware | RO |  |  | x
3xxxx | 34018 | 34018 | 03,04 | TBD | 1 | 1 | 2 | 1 |  | RO |  |  | x
3xxxx | 34019 | 34019 | 03,04 | TBD | 1 | 1 | 2 | 1 |  | RO |  |  | x
3xxxx | 34020 | 34020 | 03,04 | Temperature C | 1 | 1 | 2 | 1 | temperature C : -10 to 85 C | RO |  |  | x
3xxxx | 34021 | 34021 | 03,04 | Temperature F | 1 | 1 | 2 | 1 | temperature F : 14 to 185 F | RO |  |  | x
3xxxx | 34022 | 34022 | 03,04 | Processor Usage | 1 | 1 | 2 | 1 | percentage bandwidth used (0.1%) | RO |  |  | x
3xxxx | 34023 | 34024 | 03,04 | Event Status | 2 | 1 | 4 | 2 | TBD | RO |  |  | x
3xxxx | 34025 | 34025 | 03,04 | Communications Loss Timer | 1 | 1 | 2 | 1 | 1-600 seconds: defalt 120 seconds | RO |  |  | x
3xxxx | 34026 | 34028 | 03,04 | Power Loss Date-Time | 3 | 1 | 6 | 3 | format | RO |  |  | x
3xxxx | 34029 | 34031 | 03,04 | Power Restored Date-Time | 3 | 1 | 6 | 3 | format | RO |  |  | x
3xxxx | 34032 | 34034 | 03,04 | Firmware Build Time | 3 | 1 | 6 | 3 | format | RO |  |  | x
3xxxx | 34035 | 34035 | 03,04 | Modbus File 0 Record Size | 1 | 1 | 2 | 1 | 0 - 128 | RO |  |  | x
3xxxx | 34036 | 34036 | 03,04 | DLF Modified Application Version | 1 | 1 | 2 | 1 | DLF App Version | RO |  |  | x
3xxxx | 34037 | 34037 | 03,04 | DLF Modified Application Revision | 1 | 1 | 2 | 1 | DLF App Revision | RO |  |  | x
3xxxx | 34038 | 34038 | 03,04 | DLF Modified Download Version | 1 | 1 | 2 | 1 | DLF Download Version | RO |  |  | x
3xxxx | 34039 | 34039 | 03,04 | DLF Modified Download Revision | 1 | 1 | 2 | 1 | DLF Download Revision | RO |  |  | x
| 60001 |  |  | 1x References
3xxxx | 60001 | 60016 | 01,02 | Zone Boolean State, Zones 1 - 256 | 256 | 0.0625 | 32 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60017 | 60032 | 01,02 | Zone Logic, Zones 1 - 256 | 256 | 0.0625 | 32 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60033 | 60048 | 01,02 | Zone Object State, Zones 1 - 256 | 256 | 0.0625 | 32 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60049 | 60064 | 01,02 | Zone Manual Flag, Zones 1 - 256 | 256 | 0.0625 | 32 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60065 | 60080 | 01,02 | Zone Actual State, Zones 1 - 256 | 256 | 0.0625 | 32 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60081 | 60096 | 01,02 | Zone Event State, Zones 1 - 256 | 256 | 0.0625 | 32 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60097 | 60112 | 01,02 | Zone Event Breaker, Zones 1 - 256 | 256 | 0.0625 | 32 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60113 | 60128 | 01,02 | Zone Event Sync State, Zones 1 - 256 | 256 | 0.0625 | 32 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60129 | 60144 | 01,02 | Zone Non-Responding | 256 | 0.0625 | 32 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60145 | 60160 | 01,02 | Alarm Status, Zone Object State, Zone 1 - 256 | 256 | 0.0625 | 32 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60161 | 60416 | 01,02 | Source State by Zone Shifted, Zone 1-256 | 256 | 1 | 512 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60417 | 60672 | 01,02 | Source Event by Zone Shifted, Zone 1-256 | 256 | 1 | 512 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60673 | 60928 | 01,02 | Source Manual Flag by Zone Shifted, Zone 1-256 | 256 | 1 | 512 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 60929 | 61184 | 01,02 | Source State by Zone, Zone 1-256 | 256 | 1 | 512 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 61185 | 61440 | 01,02 | Source Event by Zone, Zone 1-256 | 256 | 1 | 512 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 61441 | 61696 | 01,02 | Source Manual Flag by Zone, Zone 1-256 | 256 | 1 | 512 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 61697 | 61760 | 01,02 | Zone Source Pointer State, Zones 1 - 256, 4 sources/ zone | 1024 | 0.0625 | 128 |  | 0 = OFF, 1 = ON, | RO |  |  | x
3xxxx | 61761 | 61824 | 01,02 | Zone Source Pointer Event, Zones 1 - 256, 4 sources/ zone | 1024 | 0.0625 | 128 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 61825 | 61888 | 01,02 | Zone Source Pointer Manual Flag, Zones 1 - 256,4 sources/ zone | 1024 | 0.0625 | 128 |  | 0 = OFF, 1 = ON | RO |  |  | x
| 62001 |  |  | 1x References
3xxxx | 62001 | 62016 | 01,02 | Input Object State, Inputs 1 - 256 | 256 | 0.0625 | 2 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62017 | 62032 | 01,02 | Input Object Manual Flag, Inputs 1 - 256 | 256 | 0.0625 | 2 |  | 0 = auto, 1 = manual | RO |  |  | x
3xxxx | 62033 | 62048 | 01,02 | Alarm Status, Input Object State, Inputs 1 - 256 | 256 | 0.0625 | 2 |  | 0 = Normal*, 1 = In alarm | RO |  |  | x
3xxxx | 62049 | 62064 | 01,02 | Input Object Event, Inputs 1 - 256 | 256 | 0.0625 | 2 |  | 0 = unchanged, 1 = changed | RO |  |  | x
3xxxx | 62065 | 62080 | 01,02 | Input Object Event Sync, Inputs 1 - 256 | 256 | 0.0625 | 2 |  | 0 = unchanged, 1 = changed | RO |  |  | x
| 62091 |  |  | 1x Terminal Status
3xxxx | 62091 | 62091 | 01,02 | Terminal State, Terminals 1-16 | 16 | 0.0625 | 2 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62092 | 62092 | 01,02 | Terminal Switch State Terminals 1-16 | 16 | 0.0625 | 2 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62093 | 62093 | 01,02 | Terminal Binary Input Activity, Terminals 1-16 | 16 | 0.0625 | 2 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62094 | 62094 | 01,02 | Terminal Binary Zone Activity, Terminals 1-16 | 16 | 0.0625 | 2 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62095 | 62095 | 01,02 | Terminal Binary Sync Activity, Terminals 1-16 | 16 | 0.0625 | 2 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62096 | 62096 | 01,02 | Terminal Toggle Event, Terminals 1-16 | 16 | 0.0625 | 2 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62097 | 62097 | 01,02 | Terminal Output Status, Terminals 1-16 | 16 | 0.0625 | 2 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62098 | 62098 | 01,02 | Terminal Level Activity, Terminals 1-16 | 16 | 0.0625 | 2 |  | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62099 | 62099 | 01,02 | Terminal A/D Range Error, Terminals 1-16 | 16 | 0.0625 | 2 |  | 0 = no Error, 1 = Error | RO |  |  | x
| 62101 |  |  | 1x References
3xxxx | 62101 | 62101 | 03,04 | Bus Present, Bus Address A - 15 | 16 | 0.0625 | 2 | 1 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62102 | 62102 | 03,04 | Bus Non-Responding, Bus Address A -15 | 16 | 0.0625 | 2 | 1 | 0 = responding, 1 = not responding | RO |  |  | x
| 62103 |  |  | 1x References
3xxxx | 62103 | 62104 | 03,04 | Breaker Actual State, Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62105 | 62106 | 03,04 | Breaker Actual State, Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62107 | 62108 | 03,04 | Breaker Actual State, Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62109 | 62110 | 03,04 | Breaker Actual State, Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62111 | 62112 | 03,04 | Breaker Actual State, Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62113 | 62114 | 03,04 | Breaker Actual State, Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62115 | 62116 | 03,04 | Breaker Actual State, Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62117 | 62118 | 03,04 | Breaker Actual State, Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62119 | 62120 | 03,04 | Breaker Actual State, Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62121 | 62122 | 03,04 | Breaker Actual State, Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62123 | 62124 | 03,04 | Breaker Actual State, Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62125 | 62126 | 03,04 | Breaker Actual State, Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62127 | 62128 | 03,04 | Breaker Actual State, Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62129 | 62130 | 03,04 | Breaker Actual State, Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62131 | 62132 | 03,04 | Breaker Actual State, Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62133 | 62134 | 03,04 | Breaker Actual State, Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
| 62135 |  |  | 1x References
3xxxx | 62135 | 62136 | 03,04 | Breaker Control State, Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62137 | 62138 | 03,04 | Breaker Control State, Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62139 | 62140 | 03,04 | Breaker Control State, Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62141 | 62142 | 03,04 | Breaker Control State, Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62143 | 62144 | 03,04 | Breaker Control State, Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62145 | 62146 | 03,04 | Breaker Control State, Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62147 | 62148 | 03,04 | Breaker Control State, Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62149 | 62150 | 03,04 | Breaker Control State, Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62151 | 62152 | 03,04 | Breaker Control State, Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62153 | 62154 | 03,04 | Breaker Control State, Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62155 | 62156 | 03,04 | Breaker Control State, Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62157 | 62158 | 03,04 | Breaker Control State, Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62159 | 62160 | 03,04 | Breaker Control State, Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62161 | 62162 | 03,04 | Breaker Control State, Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62163 | 62164 | 03,04 | Breaker Control State, Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62165 | 62166 | 03,04 | Breaker Control State, Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO
| 62167 |  |  | 1x References
3xxxx | 62167 | 62168 | 03,04 | Breaker Intended State, Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62169 | 62170 | 03,04 | Breaker Intended State, Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62171 | 62172 | 03,04 | Breaker Intended State, Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62173 | 62174 | 03,04 | Breaker Intended State, Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62175 | 62176 | 03,04 | Breaker Intended State, Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62177 | 62178 | 03,04 | Breaker Intended State, Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62179 | 62180 | 03,04 | Breaker Intended State, Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62181 | 62182 | 03,04 | Breaker Intended State, Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62183 | 62184 | 03,04 | Breaker Intended State, Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62185 | 62186 | 03,04 | Breaker Intended State, Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62187 | 62188 | 03,04 | Breaker Intended State, Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62189 | 62190 | 03,04 | Breaker Intended State, Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62191 | 62192 | 03,04 | Breaker Intended State, Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62193 | 62194 | 03,04 | Breaker Intended State, Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62195 | 62196 | 03,04 | Breaker Intended State, Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62197 | 62198 | 03,04 | Breaker Intended State, Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
| 62199 |  |  | 1x References
3xxxx | 62199 | 62200 | 03,04 | Breaker Desired/Direct State, Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62201 | 62202 | 03,04 | Breaker Desired/Direct State, Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62203 | 62204 | 03,04 | Breaker Desired/Direct State, Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62205 | 62206 | 03,04 | Breaker Desired/Direct State, Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62207 | 62208 | 03,04 | Breaker Desired/Direct State, Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62209 | 62210 | 03,04 | Breaker Desired/Direct State, Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62211 | 62212 | 03,04 | Breaker Desired/Direct State, Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62213 | 62214 | 03,04 | Breaker Desired/Direct State, Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62215 | 62216 | 03,04 | Breaker Desired/Direct State, Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62217 | 62218 | 03,04 | Breaker Desired/Direct State, Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62219 | 62220 | 03,04 | Breaker Desired/Direct State, Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62221 | 62222 | 03,04 | Breaker Desired/Direct State, Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62223 | 62224 | 03,04 | Breaker Desired/Direct State, Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62225 | 62226 | 03,04 | Breaker Desired/Direct State, Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62227 | 62228 | 03,04 | Breaker Desired/Direct State, Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
3xxxx | 62229 | 62230 | 03,04 | Breaker Desired/Direct State, Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = desired state, 1 = direct control | RO |  |  | x
| 62231 |  |  | 1x References
3xxxx | 62231 | 62232 | 03,04 | Breaker Desired State, Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62233 | 62234 | 03,04 | Breaker Desired State, Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62235 | 62236 | 03,04 | Breaker Desired State, Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62237 | 62238 | 03,04 | Breaker Desired State, Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62239 | 62240 | 03,04 | Breaker Desired State, Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62241 | 62242 | 03,04 | Breaker Desired State, Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62243 | 62244 | 03,04 | Breaker Desired State, Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62245 | 62246 | 03,04 | Breaker Desired State, Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62247 | 62248 | 03,04 | Breaker Desired State, Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62249 | 62250 | 03,04 | Breaker Desired State, Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62251 | 62252 | 03,04 | Breaker Desired State, Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62253 | 62254 | 03,04 | Breaker Desired State, Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62255 | 62256 | 03,04 | Breaker Desired State, Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62257 | 62258 | 03,04 | Breaker Desired State, Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62259 | 62260 | 03,04 | Breaker Desired State, Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62261 | 62262 | 03,04 | Breaker Desired State, Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
| 62263 |  |  | 1x References
3xxxx | 62263 | 62264 | 03,04 | Breaker Present , Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62265 | 62266 | 03,04 | Breaker Present , Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62267 | 62268 | 03,04 | Breaker Present , Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62269 | 62270 | 03,04 | Breaker Present , Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62271 | 62272 | 03,04 | Breaker Present , Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62273 | 62274 | 03,04 | Breaker Present , Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62275 | 62276 | 03,04 | Breaker Present , Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62277 | 62278 | 03,04 | Breaker Present , Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62279 | 62280 | 03,04 | Breaker Present , Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62281 | 62282 | 03,04 | Breaker Present , Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62283 | 62284 | 03,04 | Breaker Present , Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62285 | 62286 | 03,04 | Breaker Present , Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62287 | 62288 | 03,04 | Breaker Present , Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62289 | 62290 | 03,04 | Breaker Present , Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62291 | 62292 | 03,04 | Breaker Present , Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
3xxxx | 62293 | 62294 | 03,04 | Breaker Present , Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = not present, 1 = present | RO |  |  | x
| 62295 |  |  | 1x References
3xxxx | 62295 | 62296 | 03,04 | Breaker Non-responding , Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62297 | 62298 | 03,04 | Breaker Non-responding , Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62299 | 62300 | 03,04 | Breaker Non-responding , Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62301 | 62302 | 03,04 | Breaker Non-responding , Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62303 | 62304 | 03,04 | Breaker Non-responding , Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62305 | 62306 | 03,04 | Breaker Non-responding , Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62307 | 62308 | 03,04 | Breaker Non-responding , Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62309 | 62310 | 03,04 | Breaker Non-responding , Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62311 | 62312 | 03,04 | Breaker Non-responding , Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62313 | 62314 | 03,04 | Breaker Non-responding , Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62315 | 62316 | 03,04 | Breaker Non-responding , Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62317 | 62318 | 03,04 | Breaker Non-responding , Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62319 | 62320 | 03,04 | Breaker Non-responding , Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62321 | 62322 | 03,04 | Breaker Non-responding , Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62323 | 62324 | 03,04 | Breaker Non-responding , Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
3xxxx | 62325 | 62326 | 03,04 | Breaker Non-responding , Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = responding, 1 = not responding | RO |  |  | x
| 62327 |  |  | 1x References
3xxxx | 62327 | 62328 | 03,04 | Breaker Blink Flag , Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62329 | 62330 | 03,04 | Breaker Blink Flag , Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62331 | 62332 | 03,04 | Breaker Blink Flag , Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62333 | 62334 | 03,04 | Breaker Blink Flag , Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62335 | 62336 | 03,04 | Breaker Blink Flag , Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62337 | 62338 | 03,04 | Breaker Blink Flag , Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62339 | 62340 | 03,04 | Breaker Blink Flag , Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62341 | 62342 | 03,04 | Breaker Blink Flag , Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62343 | 62344 | 03,04 | Breaker Blink Flag , Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62345 | 62346 | 03,04 | Breaker Blink Flag , Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62347 | 62348 | 03,04 | Breaker Blink Flag , Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62349 | 62350 | 03,04 | Breaker Blink Flag , Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62351 | 62352 | 03,04 | Breaker Blink Flag , Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62353 | 62354 | 03,04 | Breaker Blink Flag , Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62355 | 62356 | 03,04 | Breaker Blink Flag , Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62357 | 62358 | 03,04 | Breaker Blink Flag , Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
| 62359 |  |  | 1x References
3xxxx | 62359 | 62360 | 03,04 | Breaker No Delay Flag , Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62361 | 62362 | 03,04 | Breaker No Delay Flag , Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62363 | 62364 | 03,04 | Breaker No Delay Flag , Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62365 | 62366 | 03,04 | Breaker No Delay Flag , Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62367 | 62368 | 03,04 | Breaker No Delay Flag , Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62369 | 62370 | 03,04 | Breaker No Delay Flag , Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62371 | 62372 | 03,04 | Breaker No Delay Flag , Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62373 | 62374 | 03,04 | Breaker No Delay Flag , Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62375 | 62376 | 03,04 | Breaker No Delay Flag , Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62377 | 62378 | 03,04 | Breaker No Delay Flag , Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62379 | 62380 | 03,04 | Breaker No Delay Flag , Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62381 | 62382 | 03,04 | Breaker No Delay Flag , Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62383 | 62384 | 03,04 | Breaker No Delay Flag , Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62385 | 62386 | 03,04 | Breaker No Delay Flag , Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62387 | 62388 | 03,04 | Breaker No Delay Flag , Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62389 | 62390 | 03,04 | Breaker No Delay Flag , Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
| 62391 |  |  | 1x References
3xxxx | 62391 | 62392 | 03,04 | Breaker Event Sync , Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62393 | 62394 | 03,04 | Breaker Event Sync , Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62395 | 62396 | 03,04 | Breaker Event Sync , Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62397 | 62398 | 03,04 | Breaker Event Sync , Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62399 | 62400 | 03,04 | Breaker Event Sync , Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62401 | 62402 | 03,04 | Breaker Event Sync , Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62403 | 62404 | 03,04 | Breaker Event Sync , Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62405 | 62406 | 03,04 | Breaker Event Sync , Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62407 | 62408 | 03,04 | Breaker Event Sync , Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62409 | 62410 | 03,04 | Breaker Event Sync , Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62411 | 62412 | 03,04 | Breaker Event Sync , Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62413 | 62414 | 03,04 | Breaker Event Sync , Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62415 | 62416 | 03,04 | Breaker Event Sync , Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62417 | 62418 | 03,04 | Breaker Event Sync , Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62419 | 62420 | 03,04 | Breaker Event Sync , Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62421 | 62422 | 03,04 | Breaker Event Sync , Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
| 62423 |  |  | 1x References
3xxxx | 62423 | 62424 | 03,04 | Breaker Event Zone , Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62425 | 62426 | 03,04 | Breaker Event Zone , Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62427 | 62428 | 03,04 | Breaker Event Zone , Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62429 | 62430 | 03,04 | Breaker Event Zone , Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62431 | 62432 | 03,04 | Breaker Event Zone , Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62433 | 62434 | 03,04 | Breaker Event Zone , Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62435 | 62436 | 03,04 | Breaker Event Zone , Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62437 | 62438 | 03,04 | Breaker Event Zone , Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62439 | 62440 | 03,04 | Breaker Event Zone , Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62441 | 62442 | 03,04 | Breaker Event Zone , Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62443 | 62444 | 03,04 | Breaker Event Zone , Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62445 | 62446 | 03,04 | Breaker Event Zone , Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62447 | 62448 | 03,04 | Breaker Event Zone , Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62449 | 62450 | 03,04 | Breaker Event Zone , Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62451 | 62452 | 03,04 | Breaker Event Zone , Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62453 | 62454 | 03,04 | Breaker Event Zone , Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
| 62455 |  |  | 1x References
3xxxx | 62455 | 62456 | 03,04 | Breaker Event CBus , Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62457 | 62458 | 03,04 | Breaker Event CBus , Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62459 | 62460 | 03,04 | Breaker Event CBus , Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62461 | 62462 | 03,04 | Breaker Event CBus , Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62463 | 62464 | 03,04 | Breaker Event CBus , Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62465 | 62466 | 03,04 | Breaker Event CBus , Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62467 | 62468 | 03,04 | Breaker Event CBus , Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62469 | 62470 | 03,04 | Breaker Event CBus , Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62471 | 62472 | 03,04 | Breaker Event CBus , Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62473 | 62474 | 03,04 | Breaker Event CBus , Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62475 | 62476 | 03,04 | Breaker Event CBus , Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62477 | 62478 | 03,04 | Breaker Event CBus , Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62479 | 62480 | 03,04 | Breaker Event CBus , Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62481 | 62482 | 03,04 | Breaker Event CBus , Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62483 | 62484 | 03,04 | Breaker Event CBus , Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62485 | 62486 | 03,04 | Breaker Event CBus , Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
| 62487 |  |  | 1x References
3xxxx | 62487 | 62488 | 03,04 | Breaker On-time Alarm , Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62489 | 62490 | 03,04 | Breaker On-time Alarm , Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62491 | 62492 | 03,04 | Breaker On-time Alarm , Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62493 | 62494 | 03,04 | Breaker On-time Alarm , Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62495 | 62496 | 03,04 | Breaker On-time Alarm , Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62497 | 62498 | 03,04 | Breaker On-time Alarm , Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62499 | 62500 | 03,04 | Breaker On-time Alarm , Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62501 | 62502 | 03,04 | Breaker On-time Alarm , Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62503 | 62504 | 03,04 | Breaker On-time Alarm , Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62505 | 62506 | 03,04 | Breaker On-time Alarm , Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62507 | 62508 | 03,04 | Breaker On-time Alarm , Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62509 | 62510 | 03,04 | Breaker On-time Alarm , Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62511 | 62512 | 03,04 | Breaker On-time Alarm, Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62513 | 62514 | 03,04 | Breaker On-time Alarm, Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62515 | 62516 | 03,04 | Breaker On-time Alarm, Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62517 | 62518 | 03,04 | Breaker On-time Alarm, Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
| 62519 |  |  | 1x References
3xxxx | 62519 | 62520 | 03,04 | Breaker Double Blink Flag, Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62521 | 62522 | 03,04 | Breaker Double Blink Flag, Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62523 | 62524 | 03,04 | Breaker Double Blink Flag, Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62525 | 62526 | 03,04 | Breaker Double Blink Flag, Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62527 | 62528 | 03,04 | Breaker Double Blink Flag, Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62529 | 62530 | 03,04 | Breaker Double Blink Flag, Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62531 | 62532 | 03,04 | Breaker Double Blink Flag, Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62533 | 62534 | 03,04 | Breaker Double Blink Flag,, Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62535 | 62536 | 03,04 | Breaker Double Blink Flag,, Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62537 | 62538 | 03,04 | Breaker Double Blink Flag, Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62539 | 62540 | 03,04 | Breaker Double Blink Flag, Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62541 | 62542 | 03,04 | Breaker Double Blink Flag, Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62543 | 62544 | 03,04 | Breaker Double Blink Flag, Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62545 | 62546 | 03,04 | Breaker Double Blink Flag, Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62547 | 62548 | 03,04 | Breaker Double Blink Flag, Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62549 | 62550 | 03,04 | Breaker Double Blink Flag, Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
| 62551 |  |  | 1x References
3xxxx | 62551 | 62552 | 03,04 | Breaker Change Desired State, Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62553 | 62554 | 03,04 | Breaker Change Desired State, Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62555 | 62556 | 03,04 | Breaker Change Desired State, Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62557 | 62558 | 03,04 | Breaker Change Desired State, Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62559 | 62560 | 03,04 | Breaker Change Desired State, Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62561 | 62562 | 03,04 | Breaker Change Desired State, Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62563 | 62564 | 03,04 | Breaker Change Desired State, Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62565 | 62566 | 03,04 | Breaker Change Desired State, Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62567 | 62568 | 03,04 | Breaker Change Desired State, Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62569 | 62570 | 03,04 | Breaker Change Desired State, Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62571 | 62572 | 03,04 | Breaker Change Desired State, Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62573 | 62574 | 03,04 | Breaker Change Desired State, Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62575 | 62576 | 03,04 | Breaker Change Desired State, Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62577 | 62578 | 03,04 | Breaker Change Desired State, Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62579 | 62580 | 03,04 | Breaker Change Desired State, Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62581 | 62582 | 03,04 | Breaker Change Desired State, Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
| 62583 |  |  | 1x References
3xxxx | 62583 | 62584 | 03,04 | Breaker Change Mapped, Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62585 | 62586 | 03,04 | Breaker Change Mapped, Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62587 | 62588 | 03,04 | Breaker Change Mapped, Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62589 | 62590 | 03,04 | Breaker Change Mapped, Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62591 | 62592 | 03,04 | Breaker Change Mapped, Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62593 | 62594 | 03,04 | Breaker Change Mapped, Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62595 | 62596 | 03,04 | Breaker Change Mapped, Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62597 | 62598 | 03,04 | Breaker Change Mapped, Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62599 | 62600 | 03,04 | Breaker Change Mapped, Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62601 | 62602 | 03,04 | Breaker Change Mapped, Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62603 | 62604 | 03,04 | Breaker Change Mapped, Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62605 | 62606 | 03,04 | Breaker Change Mapped, Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62607 | 62608 | 03,04 | Breaker Change Mapped, Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62609 | 62610 | 03,04 | Breaker Change Mapped, Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62611 | 62612 | 03,04 | Breaker Change Mapped, Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62613 | 62614 | 03,04 | Breaker Change Mapped, Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
| 62615 |  |  | 1x References
3xxxx | 62615 | 62616 | 03,04 | Breaker Change Control State, Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62617 | 62618 | 03,04 | Breaker Change Control State, Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62619 | 62620 | 03,04 | Breaker Change Control State, Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62621 | 62622 | 03,04 | Breaker Change Control State, Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62623 | 62624 | 03,04 | Breaker Change Control State, Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62625 | 62626 | 03,04 | Breaker Change Control State, Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62627 | 62628 | 03,04 | Breaker Change Control State, Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62629 | 62630 | 03,04 | Breaker Change Control State, Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62631 | 62632 | 03,04 | Breaker Change Control State, Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62633 | 62634 | 03,04 | Breaker Change Control State, Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62635 | 62636 | 03,04 | Breaker Change Control State, Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62637 | 62638 | 03,04 | Breaker Change Control State, Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62639 | 62640 | 03,04 | Breaker Change Control State, Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62641 | 62642 | 03,04 | Breaker Change Control State, Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62643 | 62644 | 03,04 | Breaker Change Control State, Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
3xxxx | 62645 | 62646 | 03,04 | Breaker Change Control State, Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = OFF, 1 = ON | RO |  |  | x
| 62647 |  |  | 1x References
3xxxx | 62647 | 62648 | 03,04 | Breaker Triple Blink Flag, Bus Address A | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62649 | 62650 | 03,04 | Breaker Triple Blink Flag, Bus Address B | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62651 | 62652 | 03,04 | Breaker Triple Blink Flag, Bus Address C | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62653 | 62654 | 03,04 | Breaker Triple Blink Flag, Bus Address D | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62655 | 62656 | 03,04 | Breaker Triple Blink Flag, Bus Address E | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62657 | 62658 | 03,04 | Breaker Triple Blink Flag, Bus Address F | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62659 | 62660 | 03,04 | Breaker Triple Blink Flag, Bus Address G | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62661 | 62662 | 03,04 | Breaker Triple Blink Flag,, Bus Address H | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62663 | 62664 | 03,04 | Breaker Triple Blink Flag,, Bus Address I | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62665 | 62666 | 03,04 | Breaker Triple Blink Flag, Bus Address J | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62667 | 62668 | 03,04 | Breaker Triple Blink Flag, Bus Address K | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62669 | 62670 | 03,04 | Breaker Triple Blink Flag, Bus Address L | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62671 | 62672 | 03,04 | Breaker Triple Blink Flag, Bus Address M | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62673 | 62674 | 03,04 | Breaker Triple Blink Flag, Bus Address N | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62675 | 62676 | 03,04 | Breaker Triple Blink Flag, Bus Address O | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
3xxxx | 62677 | 62678 | 03,04 | Breaker Triple Blink Flag, Bus Address P | 32 | 0.0625 | 4 | 2 | 0 = don't blink, 1 = blink | RO |  |  | x
[5 empty] | 1013 | 201 | 2026 | 1013 | Total Registers per Reference Type
Configuration Registers
4xxxx "Holding Registers" (2 Byte)
| 20001 |  |  | Terminal Configuration
4xxxx | 20001 | 20016 | 03,04 | Terminal Type, Terminals 1-16 | 16 | 1 | 32 | 16 | terminal type | RD/CW |  |  | x
4xxxx | 20017 | 20032 | 03,04 | Terminal Switch Type, Terminals 1-16 | 16 | 1 | 32 | 16 | terminal switch type | RD/CW |  |  | x
4xxxx | 20033 | 20048 | 03,04 | Terminal Sensor Type, Terminals 1-16 | 16 | 1 | 32 | 16 | terminal sensor type | RD/CW |  |  | x
4xxxx | 20049 | 20080 | 03,04 | Terminal Sensor Offset, Terminals 1-16 | 32 | 1 | 64 | 32 | terminal sensor offset | RD/CW |  |  | x
4xxxx | 20081 | 20112 | 03,04 | Terminal Sensor Scalar, Terminals 1-16 | 32 | 1 | 64 | 32 | terminal sensor scalar | RD/CW |  |  | x
4xxxx | 20113 | 20128 | 03,04 | Terminal Status Output Source, Terminals 1-16 | 16 | 1 | 32 | 16 | status output source type | RD/CW |  |  | x
4xxxx | 20129 | 20144 | 03,04 | Terminal Status Output Source Number, Terminals 1-16 | 16 | 1 | 32 | 16 | status output source number | RD/CW |  |  | x
4xxxx | 20145 | 20160 | 03,04 | Terminal Status Output Bus Number, Terminals 1-16 | 16 | 1 | 32 | 16 | status output source number | RD/CW |  |  | x
4xxxx | 20161 | 20176 | 03,04 | Terminal Number of ADC Averages, Terminals 1-16 | 16 | 1 | 32 | 16 | 1-255: default 10 | RD/CW |  |  | x
| 20301 |  |  | Input Configuration
4xxxx | 20301 | 20556 | 03,04 | Input Terminal Source, Inputs 1-256 | 256 | 1 | 512 | 256 | 0=not used, 1-16 assigned terminals 1-16*, 17-256 = 0* | RD/CW |  |  | x
4xxxx | 20557 | 20812 | 03,04 | Input Auto/Manual, Inputs 1-256 | 256 | 1 | 512 | 256 | 0-auto, 1-manual* | RD/CW |  |  | x
4xxxx | 20813 | 21068 | 03,04 | Input Timer Type, Inputs 1-256 | 256 | 1 | 512 | 256 | timer types | RD/CW |  |  | x
4xxxx | 21069 | 21324 | 03,04 | Input Timer Duration, Inputs 1-256 | 256 | 1 | 512 | 256 | 0* - 64800, units = seconds | RD/CW |  |  | x
4xxxx | 21325 | 21580 | 03,04 | Input Threshold High, Inputs 1-256 | 256 | 1 | 512 | 256 | 1 - 255 counts, 1* | RD/CW |  |  | x
4xxxx | 21581 | 21836 | 03,04 | Input Threshold Low Inputs 1-256 | 256 | 1 | 512 | 256 | 0 - 252 counts, 0* | RD/CW |  |  | x
4xxxx | 21837 | 22092 | 03,04 | Input Cbus Source Value, Input 1 - 256 | 256 | 1 | 512 | 256 | 0 - 255 counts, 255*=not used | RD/CW |  |  | x
4xxxx | 22093 | 22348 | 03,04 | Input DMX Source Value, Input 1 - 256 | 256 | 1 | 512 | 256 | 0 - 512 counts, 0*=not used | RD/CW |  |  | x
4xxxx | 22349 | 22604 | 03,04 | Input Sync Source Type, Input 1 - 256 | 256 | 1 | 512 | 256 | Sync Source Type | RD/CW |  |  | x
4xxxx | 22605 | 22860 | 03,04 | Input Sync Source Number, Input 1 - 256r | 256 | 1 | 512 | 256 | Sync Source Number | RD/CW |  |  | x
4xxxx | 22861 | 23116 | 03,04 | Input Sync Source Bus, Input 1 - 256 | 256 | 1 | 512 | 256 | Sync Source Bus | RD/CW |  |  | x
4xxxx | 23117 | 23372 | 03,04 | Input Sync Filter, Input 1 - 256 | 256 | 1 | 512 | 256 | Sync Filter | RD/CW |  |  | x
4xxxx | 23373 | 23628 | 03,04 | Input Sync Invert, Input 1 - 256 | 256 | 1 | 512 | 256 | Sync Invert | RD/CW |  |  | x
4xxxx | 23629 | 23884 | 03,04 | Input Inhibit Sync Source Type, Input 1 - 256 | 256 | 1 | 512 | 256 | Inhibit Sync Source Type | RD/CW |  |  | x
4xxxx | 23885 | 24140 | 03,04 | Input Inhibit Sync Source Number, Input 1 - 256 | 256 | 1 | 512 | 256 | Inhibit Sync Source Number | RD/CW |  |  | x
4xxxx | 24141 | 24396 | 03,04 | Input Inhibit Sync Source Bus, Input 1 - 256 | 256 | 1 | 512 | 256 | Inhibit Sync Source Bus | RD/CW |  |  | x
4xxxx | 24397 | 24652 | 03,04 | Input Inhibit Sync Filter, Input 1 - 256 | 256 | 1 | 512 | 256 | Inhibit Sync Filter | RD/CW |  |  | x
4xxxx | 24653 | 24908 | 03,04 | Input Inhibit Sync Invert, Input 1 - 256 | 256 | 1 | 512 | 256 | Inhibit Sync Invert | RD/CW |  |  | x
4xxxx | 24909 | 25164 | 03,04 | Input Timer Inhibit Sync Source Type, Input 1 - 256 | 256 | 1 | 512 | 256 | Timer Sync Source Type | RD/CW |  |  | x
4xxxx | 25165 | 25420 | 03,04 | Input Timer Inhibit Sync Source Number, Input 1 - 256 | 256 | 1 | 512 | 256 | Timer Sync Source Number | RD/CW |  |  | x
4xxxx | 25421 | 25676 | 03,04 | Input Timer Inhibit Sync Source Bus, Input 1 - 256 | 256 | 1 | 512 | 256 | Timer Sync Source Bus | RD/CW |  |  | x
4xxxx | 25677 | 25932 | 03,04 | Input Timer Inhibit Sync Filter, Input 1 - 256 | 256 | 1 | 512 | 256 | Timer Sync Filter | RD/CW |  |  | x
4xxxx | 25933 | 26188 | 03,04 | Input Timer Inhibit Sync Invert, Input 1 - 256 | 256 | 1 | 512 | 256 | Timer Sync Invert | RD/CW |  |  | x
4xxxx | 26189 | 26444 | 03,04 | Input Level Manual Value, Input 1 - 256 | 256 | 1 | 512 | 256 | 0* -255 counts | RD/WR |  |  | x
4xxxx | 26445 | 26700 | 03,04 | Input Level Auto Value, Input 1 - 256 | 256 | 1 | 512 | 256 | 0* - 255 counts | RD/WR |  |  | x
4xxxx | 26801 |  |  | Zone Configuration
4xxxx | 26801 | 27056 | 03,04 | Zone Logic Type, Zones 1-256 | 256 | 1 | 512 | 256 | Logic Type | RD/CW |  |  | x
4xxxx | 27057 | 27312 | 03,04 | Zone Truth Tables, Zones 1-256 | 256 | 1 | 512 | 256 | Truth Table | RD/CW |  |  | x
4xxxx | 27313 | 27568 | 03,04 | Zone Last Event Logic, 1-256 | 256 | 1 | 512 | 256 | Last Event | RD/CW |  |  | x
4xxxx | 27569 | 27824 | 03,04 | Zone Action on Comms Timeout, Zones 1-256 | 256 | 1 | 512 | 256 | Comms Loss Action | RD/CW |  |  | x
4xxxx | 27825 | 28080 | 03,04 | Zone Action on CommsRestore, Zones 1-256 | 256 | 1 | 512 | 256 | Comms Restore Action | RD/CW |  |  | x
4xxxx | 28081 | 28336 | 03,04 | Zone Override Timer Set point, Zones 1-256 | 256 | 1 | 512 | 256 | 0*-64800 | RD/CW |  |  | x
4xxxx | 28337 | 28592 | 03,04 | Zone Action/Priority | 256 | 1 | 512 | 256 | Action Priority | RD/CW |  |  | x
| 28593 | 28848 | 03,04 | Zone Combo Logic Polarity | 256 | 1 | 512 | 256 | 1=Zone On, 0*=Zone Off | RD/CW |  |  | x
| 30001 |  |  | Breaker Blink Configuration
4xxxx | 30001 | 30024 | 03,04 | Breaker Blink Type, Bus 0, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30025 | 30048 | 03,04 | Breaker Blink Type, Bus 1, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30049 | 30072 | 03,04 | Breaker Blink Type, Bus 2, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30073 | 30096 | 03,04 | Breaker Blink Type, Bus 3, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30097 | 30120 | 03,04 | Breaker Blink Type, Bus 4, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30121 | 30144 | 03,04 | Breaker Blink Type, Bus 5, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30145 | 30168 | 03,04 | Breaker Blink Type, Bus 6, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30169 | 30192 | 03,04 | Breaker Blink Type, Bus 7, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30193 | 30216 | 03,04 | Breaker Blink Type, Bus 8, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30217 | 30240 | 03,04 | Breaker Blink Type, Bus 9, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30241 | 30264 | 03,04 | Breaker Blink Type, Bus 10, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30265 | 30288 | 03,04 | Breaker Blink Type, Bus 11, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30289 | 30312 | 03,04 | Breaker Blink Type, Bus 12, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30313 | 30336 | 03,04 | Breaker Blink Type, Bus 13, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30337 | 30360 | 03,04 | Breaker Blink Type, Bus 14, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
4xxxx | 30361 | 30384 | 03,04 | Breaker Blink Type, Bus 15, breakers 1-24 | 24 | 1 | 48 | 24 | blink types | RD/CW |  |  | x
| 30401 |  |  | Breaker On-Time Configuration & Status
4xxxx | 30401 | 30448 | 03,04 | Total Breaker On-Time, Bus Address A | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 30449 | 30496 | 03,04 | Total Breaker On-Time, Bus Address B | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 30497 | 30544 | 03,04 | Total Breaker On-Time, Bus Address C | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 30545 | 30592 | 03,04 | Total Breaker On-Time, Bus Address D | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 30593 | 30640 | 03,04 | Total Breaker On-Time, Bus Address E | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 30641 | 30688 | 03,04 | Total Breaker On-Time, Bus Address F | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 30689 | 30736 | 03,04 | Total Breaker On-Time, Bus Address G | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 30737 | 30784 | 03,04 | Total Breaker On-Time, Bus Address H | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 30785 | 30832 | 03,04 | Total Breaker On-Time, Bus Address I | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 30833 | 30880 | 03,04 | Total Breaker On-Time, Bus Address J | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 30881 | 30928 | 03,04 | Total Breaker On-Time, Bus Address K | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 30929 | 30976 | 03,04 | Total Breaker On-Time, Bus Address L | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 30977 | 31024 | 03,04 | Total Breaker On-Time, Bus Address M | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 31025 | 31072 | 03,04 | Total Breaker On-Time, Bus Address N | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 31073 | 31120 | 03,04 | Total Breaker On-Time, Bus Address O | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 31121 | 31168 | 03,04 | Total Breaker On-Time, Bus Address P | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
| 31201 |  |  | Breaker On-Time Alarm Configuration
4xxxx | 31201 | 31248 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address A | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31249 | 31296 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address B | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31297 | 31344 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address C | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31345 | 31392 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address D | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31393 | 31440 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address E | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31441 | 31488 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address F | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31489 | 31536 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address G | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31537 | 31584 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address H | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31585 | 31632 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address I | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31633 | 31680 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address J | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31681 | 31728 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address K | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31729 | 31776 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address L | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31777 | 31824 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address M | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31825 | 31872 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address N | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31873 | 31920 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address O | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
4xxxx | 31921 | 31968 | 03,04 | Alarm Set point, Total Breaker On-Time, Bus Address P | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CW |  |  | x
| 32001 |  |  | Breaker Strike Count Configuration & Status
4xxxx | 32001 | 32048 | 03,04 | Breaker Strike Count, Bus 0, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32049 | 32096 | 03,04 | Breaker Strike Count, Bus 1, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32097 | 32144 | 03,04 | Breaker Strike Count, Bus 2, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32145 | 32192 | 03,04 | Breaker Strike Count, Bus 3, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32193 | 32240 | 03,04 | Breaker Strike Count, Bus 4, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32241 | 32288 | 03,04 | Breaker Strike Count, Bus 5, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32289 | 32336 | 03,04 | Breaker Strike Count, Bus 6, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32337 | 32384 | 03,04 | Breaker Strike Count, Bus 7, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32385 | 32432 | 03,04 | Breaker Strike Count, Bus 8, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32433 | 32480 | 03,04 | Breaker Strike Count, Bus 9, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32481 | 32528 | 03,04 | Breaker Strike Count, Bus 10, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32529 | 32576 | 03,04 | Breaker Strike Count, Bus 11, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32577 | 32624 | 03,04 | Breaker Strike Count, Bus 12, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32625 | 32672 | 03,04 | Breaker Strike Count, Bus 13, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32673 | 32720 | 03,04 | Breaker Strike Count, Bus 14, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
4xxxx | 32721 | 32768 | 03,04 | Breaker Strike Count, Bus 15, breakers 1-24 | 24 | 2 | 96 | 48 | *0 - 232, units = minutes, | RD/CmdIfWR |  |  | x
| 34901 |  |  | System/Misc Configuration
4xxxx | 34901 | 34901 | 03,04 | Blink-to-OFF Delay | 1 | 1 | 2 | 1 | Blink to Off | RD/CW |  |  | x
4xxxx | 34902 | 34902 | 03,04 | Stagger Delay | 1 | 1 | 2 | 1 | Stagger Delay | RD/CW |  |  | x
4xxxx | 34903 | 34903 | 03,04 | Breaker Verification Delay | 1 | 1 | 2 | 1 | Breaker Verification | RD/CW |  |  | x
4xxxx | 34904 | 34904 | 03,04 | Disable Coil Writes | 1 | 1 | 2 | 1 | 0x9876: Disable Coil Writes; any other value: Enables Coil Writes. Default:0x0 | RD/CW |  |  | x
4xxxx | 34905 | 34905 | 03,04 | Front Panel Password, level 1 | 1 | 1 | 2 | 1 | password | RD/CW |  |  | x
4xxxx | 34906 | 34906 | 03,04 | Front Panel Password, level 2 | 1 | 1 | 2 | 1 | password | RD/CW |  |  | x
4xxxx | 34907 | 34907 | 03,04 | Front Panel Password, level 3 | 1 | 1 | 2 | 1 | password | RD/CW |  |  | x
4xxxx | 34908 | 34908 | 03,04 | Front Panel Time Out | 1 | 1 | 2 | 1 | 1-600: units = seconds; default = 120 | RD/CW |  |  | x
4xxxx | 34909 | 34909 | 03,04 | Sweep switch pulse width | 1 | 1 | 2 | 1 | 1-10: units = seconds; default = 5 | RD/CW |  |  | x
4xxxx | 34910 | 34910 | 03,04 | Sweep switch repeat interval | 1 | 1 | 2 | 1 | 1-240: units = minutes; default = 120 | RD/CW |  |  | x
4xxxx | 34911 | 34911 | 03,04 | Communications Loss Timer Setpoint | 1 | 1 | 2 | 1 | 1-600 seconds: defalt 120 seconds | RD/CW |  |  | x
4xxxx | 34912 | 34912 | 03,04 | Communications Loss Enable | 1 | 1 | 2 | 1 | disable = 0, Modbus=1, BACnet=2, DMX=3 | RD/CW |  |  | x
4xxxx | 34913 | 34913 | 03,04 | Hardware Bus/Breaker Status Error Counter | 1 | 1 | 2 | 1 | 0 - 65535 - Increment when hardware changes | RD/WR |  |  | x
| 35001 |  |  | Manufacturing Configuration
4xxxx | 35001 | 35002 | 03,04 | Serial Number | 1 | 2 | 4 | 2 | defined by mfg | RD/PW |  |  | x
4xxxx | 35003 | 35004 | 03,04 | Hardware Series | 1 | 2 | 4 | 2 | defined by mfg - ASCII chars | RD/PW |  |  | x
4xxxx | 35005 | 35005 | 03,04 | Original Model | 1 | 1 | 2 | 1 | model shipped as | RD/PW |  |  | x
4xxxx | 35006 | 35008 | 03,04 | Date of Manufacture | 1 | 3 | 6 | 3 | format | RD/PW |  |  | x
4xxxx | 35009 | 35011 | 03,04 | MAC Address | 1 | 3 | 6 | 3 | defined by mfg | RD/PW |  |  | x
4xxxx | 35012 | 35012 | 03,04 | Manufacturing Information - Current Model | 1 | 1 | 2 | 1 | 3500 | RD/PW |  |  | x
| 35013 | 35015 | 03,04 | Manufacturing Information - Date of Model Upgrade | 1 | 3 | 6 | 3 | format | RD/PW
| 35016 | 35016 | 03,04 | Manufacturing Information - RSC Mode Enable | 1 | 1 | 2 | 1 | enable=0xAA | RD/PW
| 35017 | 35100 | 03,04 | Manufacturing Information | 1 | 84 | 168 | 84 | Manufacturing information | RD/PW
| 35201 |  |  | Clock/Calendar Configuration
4xxxx | 35201 | 35206 | 03,04 | Expanded Local Date/Time | 1 | 6 | 12 | 6 | format | RO |  |  | x
4xxxx | 35207 | 35212 | 03,04 | Expanded UTC Date/Time | 1 | 6 | 12 | 6 | format | RO |  |  | x
4xxxx | 35213 | 35215 | 03,04 | Compressed Local Date/Time | 1 | 3 | 6 | 3 | format | RO |  |  | x
4xxxx | 35216 | 35218 | 03,04 | Compressed UTC Date/Time | 1 | 3 | 6 | 3 | format | RO |  |  | x
4xxxx | 35219 | 35219 | 03,04 | Display Time Format (12/24) | 1 | 1 | 2 | 1 | value | RD/CW |  |  | x
4xxxx | 35220 | 35220 | 03,04 | Time Zone Reference | 1 | 1 | 2 | 1 | value | RD/CW |  |  | x
4xxxx | 35221 | 35221 | 03,04 | Latitude | 1 | 1 | 2 | 1 | range | RD/CW |  |  | x
4xxxx | 35222 | 35222 | 03,04 | Longitude | 1 | 1 | 2 | 1 | range | RD/CW |  |  | x
4xxxx | 35223 | 35223 | 03,04 | Daylight Saving Time Enable | 1 | 1 | 2 | 1 | 0=disable, 1*=enabled | RD/CW |  |  | x
4xxxx | 35224 | 35226 | 03,04 | US "New" (2007-on) Rule, Start | 1 | 3 | 6 | 3 | month, week, day of week week: 1-5; 1=1st, 5=last day of week: 0 - 6 (0 = Sunday) month:1-12 defaults: 2, 0, 3 (2nd Sunday March) | RD/CW |  |  | x
4xxxx | 35227 | 35229 | 03,04 | US "New" (2007-on) Rule, End | 1 | 3 | 6 | 3 | month, week, day of week week: 1-5; 1=1st, 5=last day of week: 0 - 6 (0 = Sunday) month:1-12 defaults: 1, 0, 11 (1st Sunday November) | RD/CW |  |  | x
| 35301 |  |  | NTP Time Sync Configuration
4xxxx | 35301 | 35301 | 03,04 | SNTP Port 0 | 1 | 1 | 2 | 1 | 1-65535, default = 123* | RD/CW |  |  | x
4xxxx | 35302 | 35302 | 03,04 | SNTP Port 1 | 1 | 1 | 2 | 1 | 1-65535, default = 123* | RD/CW |  |  | x
4xxxx | 35303 | 35303 | 03,04 | SNTP Time Update Interval | 1 | 1 | 2 | 1 | 1-24, units = hours | RD/CW |  |  | x
4xxxx | 35304 | 35305 | 03,04 | SNTP (time) Server (primary) IP | 1 | 2 | 4 | 2 | default: 000.000.000.000 | RD/CW |  |  | x
4xxxx | 35306 | 35307 | 03,04 | SNTP (time) Server (secondary) IP | 1 | 2 | 4 | 2 | default: 000.000.000.000 | RD/CW |  |  | x
| 35401 |  |  | Communications Port Configuration
4xxxx | 35401 | 35402 | 03,04 | Slave RS232 Port Baud Rate | 2 | 1 | 4 | 2 | baud rates | RD/CW |  |  | x
4xxxx | 35403 | 35403 | 03,04 | Slave RS232 Port Parity | 1 | 1 | 2 | 1 | 0 = none, 1 = odd, 2 = even, default = 0 | RD/CW |  |  | x
4xxxx | 35404 | 35404 | 03,04 | Slave RS232 Port Communications Mode | 1 | 1 | 2 | 1 | RS232 modes | RD/CW |  |  | x
4xxxx | 35405 | 35406 | 03,04 | Slave RS485 Port Baud Rate | 2 | 1 | 4 | 2 | baud rates | RD/CW |  |  | x
4xxxx | 35407 | 35407 | 03,04 | Slave RS485 Port Parity | 1 | 1 | 2 | 1 | 0 = none, 1 = odd, 2 = even default = 0 | RD/CW |  |  | x
4xxxx | 35408 | 35408 | 03,04 | Slave RS485 Port Communications Mode | 1 | 1 | 2 | 1 | RS485 modes | RD/CW |  |  | x
4xxxx | 35409 | 35410 | 03,04 | Local IP Address | 1 | 2 | 4 | 2 | default = Transparent Ready TR_013 | RD/CW |  |  | x
4xxxx | 35411 | 35412 | 03,04 | Local Subnet Mask | 1 | 2 | 4 | 2 | default = Transparent Ready TR_013 | RD/CW |  |  | x
4xxxx | 35413 | 35414 | 03,04 | Local Gateway Address | 1 | 2 | 4 | 2 | default = Transparent Ready TR_013 | RD/CW |  |  | x
4xxxx | 35415 | 35415 | 03,04 | TCP Connection Timeout | 1 | 1 | 2 | 1 | 1 - 32767, units = 1s, default = 300 | RD/CW |  |  | x
4xxxx | 35416 | 35416 | 03,04 | TCP Read Timeout | 1 | 1 | 2 | 1 | 1 - 32767, units = 10 ms, default = 10 | RD/CW |  |  | x
4xxxx | 35417 | 35417 | 03,04 | TCP Write Timeout | 1 | 1 | 2 | 1 | 1 - 32767, units = 10 ms, default = 10 | RD/CW |  |  | x
| 35501 |  |  | Modbus Configuration
4xxxx | 35501 | 35501 | 03,04 | Modbus Address | 1 | 1 | 2 | 1 | 1-247, default = 248 | RD/CW |  |  | x
4xxxx | 35502 | 35502 | 03,04 | Modbus Gateway timeout | 1 | 1 | 2 | 1 | 1-65535, units = seconds, default = 1s | RD/CW |  |  | x
4xxxx | 35503 | 35503 | 03,04 | Modbus Gateway Packet Interval | 1 | 1 | 2 | 1 | 1-65535, units = 10ms, default = 1 (10ms) | RD/CW |  |  | x
4xxxx | 35504 | 35504 | 03,04 | Modbus Gateway Character Timeout | 1 | 1 | 2 | 1 | 4-8, units = characters times, default = 4 | RD/CW |  |  | x
| 35551 |  |  | Smartbus Configuration
4xxxx | 35551 | 35552 | 03,04 | Smartbus RS485 Port Baud Rate | 2 | 1 | 4 | 2 | baud rates - 19200 | RO |  |  | x
4xxxx | 35553 | 35553 | 03,04 | Smartbus RS485 Port Parity | 1 | 1 | 2 | 1 | 0 = none | RO |  |  | x
4xxxx | 35554 | 35554 | 03,04 | Smartbus RS485 Port Communications Mode | 1 | 1 | 2 | 1 | RS485 modes | RO |  |  | x
| 35601 |  |  | BACnet Configuration
4xxxx | 35601 | 35601 | 03,04 | MSTP Address | 1 | 1 | 2 | 1 | 0-127, default: 0 | RD/CW |  |  | x
4xxxx | 35602 | 35602 | 03,04 | BACnet UDP Port | 1 | 1 | 2 | 1 | 0-65535, default: 47808 (0xBAC0) | RD/CW |  |  | x
4xxxx | 35603 | 35604 | 03,04 | BBMD IP Address | 1 | 2 | 4 | 2 | default: 000.000.000.000 | RD/CW |  |  | x
4xxxx | 35605 | 35605 | 03,04 | BACnet BBMD UDP Port | 1 | 1 | 2 | 1 | 0-65535, default: 47808 (0xBAC0) | RD/CW |  |  | x
4xxxx | 35606 | 35607 | 03,04 | Device ID | 1 | 2 | 4 | 2 | 0-4,194,302, default: last 6 digits of serial number | RD/CW |  |  | x
4xxxx | 35608 | 35608 | 03,04 | BACnet Modes | 1 | 1 | 2 | 1 | bits 15-4: reserved, default 0; bit 3: breaker objects; 0: disable*, 1: enable bit 2, control; 0: disable*, 1: enable bit 1, mode; 0: BIP, 1: MSTP bit 0, enable; 0: disable BACnet, 1: enable BACnet | RD/CW |  |  | x
4xxxx | 35609 | 35609 | 03,04 | APDU Timeout | 1 | 1 | 2 | 1 | 100-255, default: 200, units: 10 msec | RD/CW |  |  | x
4xxxx | 35610 | 35610 | 03,04 | APDU Retries | 1 | 1 | 2 | 1 | 1-5, default: 3 | RD/CW |  |  | x
4xxxx | 35611 | 35611 | 03,04 | BBMD Time-to-live | 1 | 1 | 2 | 1 | 100-65535, default: 300, units: s | RD/CW |  |  | x
| 48000 |  |  | Production Communications Interface
4xxxx | 48000 | 48000 | 03,04 | Command Register | 1 | 1 | 2 | 1 | Command: 0x79E1 | RD/WR |  |  | x
4xxxx | 48001 | 48001 | 03,04 | Password Register | 1 | 1 | 2 | 1 | Password: 0x8B2D | RD/WR |  |  | x
4xxxx | 48002 | 48002 | 03,04 | Modbus Address | 1 | 1 | 2 | 1 | 1-247 | RD/WR |  |  | x
4xxxx | 48003 | 48003 | 03,04 | RS232, RS485 Baud Rate | 1 | 1 | 2 | 1 | 1=4800, 2=9600, 3=19200, 4=38400, 5=56700, 6=76800, 7=115200 | RD/WR |  |  | x
4xxxx | 48004 | 48004 | 03,04 | RS232, RS485 Parity | 1 | 1 | 2 | 1 | 0=none, 1=odd, 2=even | RD/WR |  |  | x
4xxxx | 48005 | 48005 | 03,04 | Ethernet IP Hi Word | 1 | 1 | 2 | 1 | Valid IP = 0x1 - 0xFFFFFFFE | RD/WR |  |  | x
4xxxx | 48006 | 48006 | 03,04 | Ethernet IP Lo Word | 1 | 1 | 2 | 1 |  | RD/WR |  |  | x
4xxxx | 48007 | 48007 | 03,04 | Ethernet Subnet Hi Word | 1 | 1 | 2 | 1 | Valid Subnet = 0x1 - 0xFFFFFFFE | RD/WR |  |  | x
4xxxx | 48008 | 48008 | 03,04 | Ethernet Subnet Lo Word | 1 | 1 | 2 | 1 |  | RD/WR |  |  | x
4xxxx | 48009 | 48009 | 03,04 | Ethernet Gateway Hi Word | 1 | 1 | 2 | 1 | Valid Gateway = 0x1 - 0xFFFFFFFE | RD/WR |  |  | x
4xxxx | 48010 | 48010 | 03,04 | Ethernet Gateway Lo Word | 1 | 1 | 2 | 1 |  | RD/WR |  |  | x
| 48015 |  |  | Command Interface
4xxxx | 48015 | 48015 | 03,04 | Semaphore Request | 1 | 1 | 2 | 1 | 0-not available, >0-aquired | RO |  |  | x
4xxxx | 48016 | 48016 | 03,04 | Active Access Semaphore | 1 | 1 | 2 | 1 | 0-available, >0-not available | RO |  |  | x
4xxxx | 48017 | 48017 | 03,04 | Active Command | 1 | 1 | 2 | 1 | see Command Interface Docs | RO |  |  | x
4xxxx | 48018 | 48018 | 03,04 | Prior Command | 1 | 1 | 2 | 1 | see Command Interface Docs | RO |  |  | x
4xxxx | 48019 | 48019 | 03,04 | Prior Command Result Code | 1 | 1 | 2 | 1 | Result Codes | RO |  |  | x
4xxxx | 48020 | 48020 | 03,04 | Command | 1 | 1 | 2 | 1 | see Command Interface Docs | RD/CmdIfWR |  |  | x
4xxxx | 48021 | 48029 | 03,04 | Command Parameters 1 - 9 | 9 | 1 | 18 | 9 | see Command Interface Docs | RD/CmdIfWR |  |  | x
4xxxx | 48030 | 48130 | 03,04 | Command Data Buffer Area | 101 | 1 | 202 | 101 | see Command Interface Docs | RD/CmdIfWR |  |  | x
| 48188 |  |  | ID
4xxxx | 48188 | 48188 | 03,04 | "PowerLogic" Device ID (Req'd for Compatibility) | 1 | 1 | 2 | 1 | device ID | RO |  |  | x
4xxxx | 48189 | 48189 | 03,04 | "PowerLogic" Option ID (Req'd for Compatibility) | 1 | 1 | 2 | 1 | option ID | RO |  |  | x
| 48200 |  |  | Command Interface Shortcut
4xxxx | 48200 | 48200 | 03,04 | Command Interface Shortcut | 1 | 1 | 2 | 1 | 0x2222: enable Command Interface; other: disable | RD/WR |  |  | x
| 48700 |  |  | 0x Writes
4xxxx | 0 | 0 | 03,04 | 0x Reference Writes | 1 | 1 | 2 | 1 | bits 0-14: register addressbit 15: state | RD/CW |  |  | x
| 65533 |  |  | Upgrade Key (Write Only)
4xxxx | 65533 | 65535 | 03,04 | Model Upgrade Key | 3 | 1 | 6 | 3 |  | WO |  |  | x
[5 empty] | 10187 |  | 22910 | 11455 | Total Registers per Reference Type
[5 empty] | 11200 |  | 24936 | 12468 | Total Registers
Total Bytes, All Registers
|  |  |  | 6xxxxx "General References" | Modbus function codes 20 (read); write: 21(write, in configuration mode)
| File 0 : File Size Header |  |  |  | Items | Registers | Bytes
| Record Definition | [11 empty] | x
|  |  |  | File Number 1 | 1 | 1 | 2 |  | Data Structure File 1 |  |  |  | x
|  |  |  | Number of Records - File 1 | 1 | 1 | 2 | [5 empty] | x
|  |  |  | Record Size - File 1 | 1 | 1 | 2 | [5 empty] | x
|  |  |  | File Number 2 | 1 | 1 | 2 |  | Data Structure File 2 |  |  |  | x
|  |  |  | Number of Records - File 2 | 1 | 1 | 2 | [5 empty] | x
|  |  |  | Record Size - File 2 | 1 | 1 | 2 | [5 empty] | x
|  |  |  | File Number 3 | 1 | 1 | 2 |  | Data Structure File 3 |  |  |  | x
|  |  |  | Number of Records - File 3 | 1 | 1 | 2 | [5 empty] | x
|  |  |  | Record Size - File 3 | 1 | 1 | 2 | [5 empty] | x
|  |  |  | : | : | : | : | [5 empty] | x
|  |  |  | File Number 40 | 1 | 1 | 2 |  | Data Structure File 32 |  |  |  | x
|  |  |  | Number of Records - File 40 | 1 | 1 | 2 | [5 empty] | x
|  |  |  | Record Size - File 40 | 1 | 1 | 2 | [5 empty] | x
x
|  |  |  | File Number | *40 | 40 | 80 |  | File Number |  |  |  | x
|  |  |  | Number of Records | 40 | 40 | 80 |  | 0 indicates no records |  |  |  | x
|  |  |  | Record Size | 40 | 40 | 80 |  | 0 indicates size not known |  |  |  | x
x
x
| Record Summary |  |  |  | 80 | 120 | 240 |  | *max number of file |  |  |  | x
File Definition
| Record 1 |  |  | File Size Header | 1 | 120 | 240
Total
| File 1 : Terminal Configuration |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Terminal Defined/Undefined | 1 | 0.5 | 1 |  | 0=undefined, 1=defined, default:1-16 = 1 | RD/CW |  |  | x
|  |  |  | Terminal Active/Inactive | 1 | 0.5 | 1 |  | 0=inactive, 1=active, default:1-16 = 1 | RD/CW |  |  | x
|  |  |  | Terminal Type | 1 | 1 | 2 |  | terminal type | RD/CW |  |  | x
|  |  |  | Terminal Switch Type | 1 | 1 | 2 |  | terminal switch type | RD/CW |  |  | x
|  |  |  | Terminal Sensor Type | 1 | 1 | 2 |  | terminal sensor type | RD/CW |  |  | x
|  |  |  | Terminal Sensor Offset | 1 | 2 | 4 |  | terminal sensor offset | RD/CW |  |  | x
|  |  |  | Terminal Sensor Scalar | 1 | 2 | 4 |  | terminal sensor scalar | RD/CW |  |  | x
|  |  |  | Terminal Status Output Source | 1 | 1 | 2 |  | status output source type | RD/CW |  |  | x
|  |  |  | Terminal Status Output Source Number | 1 | 1 | 2 |  | status output source number | RD/CW |  |  | x
|  |  |  | Terminal Status Output Bus | 1 | 1 | 2 |  | status ouput source bus | RD/CW |  |  | x
|  |  |  | Terminal Number of ADC Averages | 1 | 1 | 2 |  | 1-255: default 10 |  |  |  | x
| Record Summary |  |  |  | 11 | 12 | 24
File Definition
| Record 1-16 |  |  | Terminal Configuration File | 16 | 192 | 384
Total
| File 2 : Input Configuration |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Input Defined/Undefined | 1 | 0.5 | 1 |  | 0=undefined, 1=defined, default:1-16 = 1, 17-256 = 0 | RD/CW |  |  | x
|  |  |  | Input Active/Inactive | 1 | 0.5 | 1 |  | 0=inactive, 1=active, default:1-16 =1, 17-256 = 0 | RD/CW |  |  | x
|  |  |  | Input Alarm Enable | 1 | 0.5 | 1 |  | 0*=disable, 1=enable | RD/CW |  |  | x
|  |  |  | Input Alarm State | 1 | 0.5 | 1 |  | alarm on state ?, 0*, 1 | RD/CW |  |  | x
|  |  |  | Input Terminal Source | 1 | 1 | 2 |  | 0:not used, 1-16 | RD/CW |  |  | x
|  |  |  | Input Auto/Manual | 1 | 1 | 2 |  | 0-auto*, 1-manual | RD/CW |  |  | x
|  |  |  | Input Timer Type | 1 | 1 | 2 |  | timer types | RD/CW |  |  | x
|  |  |  | Input Timer Duration | 1 | 1 | 2 |  | 0* - 64800, units = seconds | RD/CW |  |  | x
|  |  |  | Input Threshold High | 1 | 1 | 2 |  | 1 -255, default = 1 | RD/CW |  |  | x
|  |  |  | Input Threshold Low | 1 | 1 | 2 |  | 0*-252 | RD/CW |  |  | x
|  |  |  | Input Cbus Source | 1 | 1 | 2 |  | 0*-255 | RD/CW |  |  | x
|  |  |  | Input Cbus Application | 1 | 1 | 2 |  | 48 - 95, default=56 | RD/CW |  |  | x
|  |  |  | Input DMX source | 1 | 1 | 2 |  | 0*-512 | RD/CW |  |  | x
|  |  |  | Input Sync Source Type *1 | 1 | 1 | 2 |  | Sync Source Type | RD/CW |  |  | x
|  |  |  | Input Sync Source Number | 1 | 1 | 2 |  | Sync Source Number | RD/CW |  |  | x
|  |  |  | Input Sync Source Bus *1 | 1 | 1 | 2 |  | Sync Source Bus | RD/CW |  |  | x
|  |  |  | Input Sync Filter *1 | 1 | 1 | 2 |  | Sync Filter | RD/CW |  |  | x
|  |  |  | Input Sync Invert *1 | 1 | 1 | 2 |  | Sync Invert | RD/CW |  |  | x
|  |  |  | Input Inhibit Sync Source Type *1 | 1 | 1 | 2 |  | Inhibit Sync Source Type | RD/CW |  |  | x
|  |  |  | Input Inhibit Sync Source Number | 1 | 1 | 2 |  | Inhibit Sync Source Number | RD/CW |  |  | x
|  |  |  | Input Inhibit Sync Source Bus *1 | 1 | 1 | 2 |  | Inhibit Sync Source Bus | RD/CW |  |  | x
|  |  |  | Input Inhibit Sync Filter *1 | 1 | 1 | 2 |  | Inhibit Sync Filter | RD/CW |  |  | x
|  |  |  | Input Inhibit Sync Invert *1 | 1 | 1 | 2 |  | Inhibit Sync Invert | RD/CW |  |  | x
|  |  |  | Input Timer Sync Source Type *1 | 1 | 1 | 2 |  | Timer Sync Source Type | RD/CW |  |  | x
|  |  |  | Input Timer Sync Source Number | 1 | 1 | 2 |  | Timer Sync Source Number | RD/CW |  |  | x
|  |  |  | Input Timer Sync Source Bus *1 | 1 | 1 | 2 |  | Timer Sync Source Bus | RD/CW |  |  | x
|  |  |  | Input Timer Sync Filter *1 | 1 | 1 | 2 |  | Timer Sync Filter | RD/CW |  |  | x
|  |  |  | Input Timer Sync Invert *1 | 1 | 1 | 2 |  | Timer Sync Invert | RD/CW |  |  | x
note *1 - msb is not validated, set to 0 by firmware
| Record Summary |  |  |  | 28 | 26 | 52
File Definition
| Record 1-256 |  |  | Input Configuration File | 256 | 6656 | 13312
Total
| File 3 : Panel Configuration |  |  |  | Items | Registers | Bytes
1 records per Panel - Panel 1 = Recored 1, Panel 2 = Record 2 etc…
Panel Configuration
|  |  |  | Panel ID | 1 | 1 | 2 |  | 0-99 | RD/CW |  |  | x
|  |  |  | Custom | 1 | 1 | 2 |  | 0-1 | RD/CW |  |  | x
|  |  |  | Inverted | 1 | 1 | 2 |  | 0-1 | RD/CW |  |  | x
|  |  |  | Starting Breaker Number | 1 | 1 | 2 |  | 1-336 | RD/CW |  |  | x
|  |  |  | Squence | 1 | 1 | 2 |  | 1-2 | RD/CW |  |  | x
|  |  |  | Bus Length A | 1 | 1 | 2 |  | 12,18,21 | RD/CW |  |  | x
|  |  |  | Bus Length B | 1 | 1 | 2 |  | 12,18,21 | RD/CW |  |  | x
|  |  |  | Bus Length C | 1 | 1 | 2 |  | 12,18,21 | RD/CW |  |  | x
|  |  |  | BusLength D | 1 | 1 | 2 |  | 12,18,21 | RD/CW |  |  | x
| Record Summary 1-8 |  |  |  | 9 | 9 | 18
File Definition
| Record 1-8 |  |  | Panel Configuration | 8 | 72 | 144 |  |  | RD/CW
Total
| File 4: Zone Configuration |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Zone Defined/Undefined | 1 | 0.5 | 1 |  | 0=undefined, 1=defined, default:1-16 defined, 17-256 undefined | RD/CW |  |  | x
|  |  |  | Zone Active/Inactive | 1 | 0.5 | 1 |  | 0=inactive, 1=active, default:1-16 active, 17-256 inactive | RD/CW |  |  | x
|  |  |  | Zone Alarm Enable | 1 | 0.5 | 1 |  | 0*=disable, 1=enable | RD/CW |  |  | x
|  |  |  | Zone Alarm State | 1 | 0.5 | 1 |  | alarm on state ?, 0*, 1 | RD/CW |  |  | x
|  |  |  | Zone Logic Type | 1 | 1 | 2 |  | Logic Type | RD/CW |  |  | x
|  |  |  | Zone Truth Table | 1 | 1 | 2 |  | Truth Table | RD/CW |  |  | x
|  |  |  | Zone Combo Logic Polarity | 1 | 1 | 2 |  | 1=Zone On, 0=Zone Off | RD/CW |  |  | x
|  |  |  | Zone Last Event | 1 | 1 | 2 |  | Last Event | RD/CW |  |  | x
|  |  |  | Zone Comms Loss Action | 1 | 1 | 2 |  | Comms Loss Action | RD/CW |  |  | x
|  |  |  | Zone Comms Restore Action | 1 | 1 | 2 |  | Comms Restore Action | RD/CW |  |  | x
|  |  |  | Zone Override Timer Setpoint | 1 | 1 | 2 |  | 0*-64800 | RD/CW |  |  | x
|  |  |  | Zone Active Priority | 1 | 1 | 2 |  | Active Priority | RD/CW |  |  | x
|  |  |  | Zone Source Pointer Set | 4 | 20 | 40 |  | Source Pointer Set | RD/CW |  |  | x
|  |  |  | Zone Member List Bus | 16 | 32 | 64 |  | Member List Bus | RD/CW |  |  | x
| Record Summary |  |  | Total | 32 | 62 | 124
[5 empty] | Items | Registers | Bytes
File Definition
| Record 1-256 |  |  | Zone Configuration | 256 | 15872 | 31744 |  |  | RD/CW
Total
File 5: Schedules
Record Definition
|  |  |  | Schedule Defined/Undefined | 1 | 0.5 | 1 |  | 0 = undefined*, 1 = defined | RD/CW |  |  | x
|  |  |  | Schedule Active/Inactive | 1 | 0.5 | 1 |  | 0 = inactive*, 1 = active | RD/CW |  |  | x
|  |  |  | Schedule Alarm Enable | 1 | 0.5 | 1 |  | 0*=disable, 1=enable | RD/CW |  |  | x
|  |  |  | Schedule Alarm State | 1 | 0.5 | 1 |  | alarm on state ?, 0*, 1 | RD/CW |  |  | x
|  |  |  | Periods | 1024 | 64 | 128 |  | Periods |  |  |  | x
x
[6 empty] | 66 | 132
File Definition
| Record 1-64 |  |  | Schedule Configuration | 64 | 4224 | 8448 |  |  | RD/CW
Total
| File 6: Period |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Period Defined/Undefined | 1 | 0.5 | 1 |  | 0 = undefined*, 1 = defined | RD/CW |  |  | x
|  |  |  | Period Active/Inactive | 1 | 0.5 | 1 |  | 0 = inactive*, 1 = active | RD/CW |  |  | x
|  |  |  | Start Time | [5 empty] | RD/CW |  |  | x
|  |  |  | start hour | 1 | 0.5 | 1 |  | start hour | RD/CW |  |  | x
|  |  |  | start minutes | 1 | 0.5 | 1 |  | start minutes | RD/CW |  |  | x
|  |  |  | start offset | 1 | 1 | 2 |  | start offset | RD/CW |  |  | x
|  |  |  | End Time | [5 empty] | RD/CW |  |  | x
|  |  |  | end hour | 1 | 0.5 | 1 |  | end hour | RD/CW |  |  | x
|  |  |  | end minutes | 1 | 0.5 | 1 |  | end minutes | RD/CW |  |  | x
|  |  |  | end offset | 1 | 1 | 2 |  | end offset | RD/CW |  |  | x
|  |  |  | Schedule Days | [5 empty] | RD/CW |  |  | x
|  |  |  | day of week | 1 | 1 | 2 |  | day of week | RD/CW |  |  | x
|  |  |  | special days | 1 | 6 | 12 |  | special days | RD/CW |  |  | x
| Record Summary, even numbered records |  |  |  | 10 | 12 | 24
File Definition
| Record 1-128 |  |  | Periods - 8 periods per record(96 registers) | 128 | 12288 | 24576 |  |  | RD/CW
Total
| File 7: Special Days |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Special Day Defined/Undefined | 1 | 0.5 | 1 |  | 0 = undefined* 1 = defined | RD/CW |  |  | x
|  |  |  | Special Day Schedule Active/Inactive | 1 | 0.5 | 1 |  | 0 = inactive* 1 = active | RD/CW |  |  | x
|  |  |  | Special Day Alarm Enable | 1 | 0.5 | 1 |  | 0*=disable, 1=enable | RD/CW |  |  | x
|  |  |  | Special Day Alarm State | 1 | 0.5 | 1 |  | alarm on state - not used | RD/CW |  |  | x
|  |  |  | Global / Non-Global Day*1 | 1 | 1 | 2 |  | 0:non global, 1:global | RD/CW |  |  | x
|  |  |  | Repeat Type *1 | 1 | 1 | 2 |  | repeat type | RD/CW |  |  | x
|  |  |  | Start Day*1 | 1 | 1 | 2 |  | start day | RD/CW |  |  | x
|  |  |  | Start Month*1 | 1 | 1 | 2 |  | start month | RD/CW |  |  | x
|  |  |  | Start Year*1 | 1 | 1 | 2 |  | start year | RD/CW |  |  | x
|  |  |  | End Day*1 | 1 | 1 | 2 |  | end day | RD/CW |  |  | x
|  |  |  | End Month*1 | 1 | 1 | 2 |  | end month | RD/CW |  |  | x
|  |  |  | End Year*1 | 1 | 1 | 2 |  | end year | RD/CW |  |  | x
|  |  |  | Day of Week*1 | 1 | 1 | 2 |  | day of week | RD/CW |  |  | x
|  |  |  | Week of Month*1 | 1 | 1 | 2 |  | week of month | RD/CW |  |  | x
|  |  |  | Month of Year*1 | 1 | 1 | 2 |  | month of year | RD/CW |  |  | x
|  |  |  | Day of Month*1 | 1 | 1 | 2 |  | day of month | RD/CW |  |  | x
|  |  |  | Through Month*1 | 1 | 1 | 2 |  | through month | RD/CW |  |  | x
|  |  |  | Though Day*1 | 1 | 1 | 2 |  | through day | RD/CW |  |  | x
|  |  |  | Priority*1 | 1 | 1 | 2 |  | priority | RD/CW |  |  | x
|  |  |  | Duration | 1 | 1 | 2 |  | duration | RD/CW |  |  | x
|  |  |  | Repeat Interval*1 | 1 | 1 | 2 |  | repeat interval | RD/CW |  |  | x
|  |  |  | Holiday*1 | 1 | 1 | 2 |  | holiday | RD/CW |  |  | x
note *1 - msb is not validated, set to 0 by firmware
| Record Summary |  |  |  | 22 | 20 | 40
File Definition
| Record 1-96 |  |  | Special Day | 96 | 20 | 3840 |  |  | RD/CW
Total
| File 8: Bus/Breaker Configuration |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Bus Panel | 1 | 1 | 2 |  | panel | RD/CW |  |  | x
|  |  |  | Bus Side - Left/Right | 1 | 1 | 2 |  | 1 = left, 2 =right | RD/CW |  |  | x
[5 empty] | 24 | 96 | 192 |  | Breaker 1-24, EL Type, Blink Type, On-Time Setpoint | RD/CW |  |  | x
|  |  |  | Bus1/Breaker1. ELType | 1 | 5 |  |  |  | RD/CW |  |  | x
|  |  |  | Bus1/Breaker1. BlinkType | 1 | 5 |  |  |  | RD/CW |  |  | x
|  |  |  | Bus1/Breaker1 Alarm Set Point | 1 | 6,7
|  |  |  | Bus1/Breaker1 On-time Alarm Enable | 0.5 | 8
|  |  |  | Bus1/Breaker1 On-time Alarm State | 0.5 | 8
|  |  |  | Bus1/Breaker2. ELType | 1 | 9 |  |  |  | RD/CW |  |  | x
|  |  |  | Bus1/Breaker2. BlinkType | 1 | 9 |  |  |  | RD/CW |  |  | x
|  |  |  | Bus1/Breaker2 Alarm Set Point | 1 | 10,11
|  |  |  | Bus1/Breaker2 On-time Alarm Enable | 0.5 | 12
|  |  |  | Bus1/Breaker2 On-time Alarm State | 0.5 | 12
|  |  |  | Bus1/Breaker24. ELType | 1 | 97 |  |  |  | RD/CW |  |  | x
|  |  |  | Bus1/Breaker24. BlinkType | 1 | 97 |  |  |  | RD/CW |  |  | x
|  |  |  | Bus1/Breaker24.Alarm Set Point | 1 | 98,99 |  |  |  | RD/CW |  |  | x
|  |  |  | Bus1/Breaker24On-time Alarm Enable | 0.5 | 100
|  |  |  | Bus1/Breaker24 On-time Alarm State | 0.5 | 100
| Record Summary |  |  |  | 26 | 100 | 200
File Definition
| Record 1-16 |  |  | Bus/Breaker Configuration | 16 | 1600 | 3200 |  |  | RD/CW
Total
File 9: Subscriber
Record Definition
|  |  |  | Defined/Undefined | 1 | 0.5 | 1 |  | 0* = undefined 1 = defined | RD/CW |  |  | x
|  |  |  | Active/Inactive | 1 | 0.5 | 1 |  | 0* = inactive 1 = active | RD/CW |  |  | x
|  |  |  | Subscriber Alarm Enable | 1 | 0.5 | 1 |  | 0*=disable, 1=enable | RD/CW |  |  | x
|  |  |  | Subscriber Alarm State | 1 | 0.5 | 1 |  | alarm on state ?, 0*, 1 | RD/CW |  |  | x
|  |  |  | Subscriber IP Address | 1 | 2 | 4 |  | default: 000.000.000.000 | RD/CW |  |  | x
|  |  |  | Subscriber Unit ID | 1 | 1 | 2 |  | ModBus Address B*-247 | RD/CW |  |  | x
|  |  |  | Subscription Number* | 1 | 1 | 2 |  | read only - binary subscription 1-64, analog subscription 65-128 | RD/CW |  |  | x
|  |  |  | Type | 1 | 1 | 2 |  | 0*-coil, 1-register | RD/CW |  |  | x
|  |  |  | Length | 1 | 1 | 2 |  | always 1 | RD/CW |  |  | x
|  |  |  | Subscribe-to Address | 1 | 1 | 2 |  | 0*-65535, 0=unsubscribe | RD/CW |  |  | x
|  |  |  | Publish-to-Address | 1 | 1 | 2 |  | 0*-65535 | RD/CW |  |  | x
|  |  |  | Heartbeat Interval | 1 | 1 | 2 |  | 60*- 7200 seconds | RD/CW |  |  | x
|  |  |  | Publisher Timeout | 1 | 1 | 2 |  | heartbeat * 5 - read only | RD/CW |  |  | x
|  |  |  | Minimum Interval | 1 | 1 | 2 |  | not used | RD/CW |  |  | x
|  |  |  | Periodic Publish Interval | 1 | 1 | 2 |  | 0-65535 seconds | RD/CW |  |  | x
|  |  |  | Publisher File Number | 1 | 1 | 2 |  | 10 - read only | RD/CW |  |  | x
|  |  |  | Default Action Value Binary | 1 | 1 | 2 |  | 0*-off/manual, 1-on/auto, 2-last event | RD/CW |  |  | x
|  |  |  | Default Action Value Analog Level | 1 | 1 | 2 |  | 0*-255, 0x8000-last event | RD/CW |  |  | x
|  |  |  | Reserved | 1 | 3 | 6 |  | n/a | RD/CW |  |  | x
| Record Summary |  |  |  | 19 | 20 | 26
File Definition
| Record 1-192 |  |  | Subscription Configuration | 192 | 3840 | 4992 |  | 64 Binary Subscriptions, two files per subscription, files 1-128. 64 Analog subscriptions, files 129-192.
| Total |  |  | *Record 1-128 - Binary, Record 129-192 Analog
File 10: Publisher
Record Definition
|  |  |  | Publisher IP Address | 1 | 2 | 4 |  | default: 000.000.000.000 | RD |  |  | x
|  |  |  | Publisher Unit ID | 1 | 0.5 | 1 |  | Modbis Address 1*-247 | RD |  |  | x
|  |  |  | Subscription Number | 1 | 0.5 | 1 |  | record number-read only | RD |  |  | x
|  |  |  | Subscription New/Changed | 1 | 0.5 |  |  | 0-no change, 1-change | RD
|  |  |  | Type | 1 | 0.5 | 1 |  | 0*-coil, 1-register | RD |  |  | x
|  |  |  | Length | 1 | 1 | 2 |  | always 1 | RD |  |  | x
|  |  |  | Subscribe-to Starting Address | 1 | 64 | 128 |  | 0*-65535, 0=unsubscribe | RD |  |  | x
|  |  |  | Publisher Timeout | 1 | 1 | 2 |  | heartbeat * 5 - read only | RD |  |  | x
|  |  |  | Minimum Interval | 1 | 1 | 2 |  | not used | RD |  |  | x
|  |  |  | Periodic Publish Interval | 1 | 1 | 2 |  | 0-65535 seconds | RD |  |  | x
|  |  |  | Shared Interface Command | 1 | 1 | 2 |  | 0x1234 - binary, 0x1235 - analog | RD |  |  | x
|  |  |  | Shared Command Interface Command Number | 1 | 0 | 0 |  | * G3 compatiblity bug not readable | RD |  |  | x
| Record Summary |  |  |  | 12 | 73 | 145
File Definition
| Record 1-512 |  |  | Publisher Configuration | 512 | 37376 | 74240
Total
File 11: Event Log
Record Overview
|  | Header for each record: |  | Year | 1 | 0.5 | 1 |  | 0-99: current year - 2000 | RD |  |  | x
|  |  |  | Month | 1 | 0.5 | 1 |  | 1-12 | RD |  |  | x
|  |  |  | Day | 1 | 0.5 | 1 |  | 1-31 | RD |  |  | x
|  |  |  | Hour | 1 | 0.5 | 1 |  | 0-23 | RD |  |  | x
|  |  |  | Minutes | 1 | 0.5 | 1 |  | 0-59 | RD |  |  | x
|  |  |  | Seconds | 1 | 0.5 | 1 |  | 0-59 | RD |  |  | x
|  |  |  | Record ID | 1 | 2 | 4 |  | 0-2^32-1 - bitmap | RD |  |  | x
|  |  |  | Event Type | 1 | 2 | 4 |  | 1=input, 2=zone, 3=zone override, 4=configuration, 5=firmware download 6=special days, 7=schedules, 8=breakers, 9=learn mode, 10=reset, 11=bus status change, 12 breaker status change | RD |  |  | x
|  |  |  | Event Size | 1 | 1 | 2 |  | number of bytes for given event type | RD |  |  | x
| Header Record Summary |  |  |  | 9 | 8 | 16 | [5 empty] | x
|  |  |  | Event Data - See EDD's for data format - All events 44 bytes in length, but vary with information, see EDDs | [5 empty] | RD |  |  | x
File Definition
| Record 1-1024 |  |  | Event Log Standard Size | 1024 | 22 | 44 |  | Each event record is the same size. The data format varies with each event type. | RD
Total
| File 12: CBUS Output |  |  |  | Items | Registers | Bytes
Record Definition
|  |  | 1 | Defined/Undefined | 1 | 0.5 | 1 |  | 0 = undefined 1 = defined | RD/CW |  |  | x
|  |  | 1 | Active/Inactive | 1 | 0.5 | 1 |  | 0 = inactive 1 = active | RD/CW |  |  | x
|  |  | 2 | Event Source Type | 1 | 1 | 2 |  | Source Type | RD/CW |  |  | x
|  |  | 3 | Event Source Number | 1 | 1 | 2 |  | Source Number | RD/CW |  |  | x
|  |  | 4 | Event Source Bus | 1 | 1 | 2 |  | Source: Breaker Bus Number 0- 15 | RD/CW |  |  | x
|  |  | 5 | Group Number | 1 | 1 | 2 |  | Group Address | RD/CW |  |  | x
|  |  | 6 | Application Number | 1 | 1 | 2 |  | App: 48-95, 0xCA, 0xCB, default 56 | RD/CW |  |  | x
|  |  | 7 | On Level Source Type | 1 | 1 | 2 |  | On Level Source | RD/CW |  |  | x
|  |  | 8 | On Level Source Number | 1 | 1 | 2 |  | On Level Source Number | RD/CW |  |  | x
|  |  | 9 | On Level Source Bus | 1 | 1 | 2 |  | Source Breaker Bus Number 0- 15 | RD/CW |  |  | x
|  |  | 10 | On Level | 1 | 1 | 2 |  | 0-255 | RD/CW |  |  | x
|  |  | 11 | On Ramp Rate | 1 | 1 | 2 |  | On Ramp Rate | RD/CW |  |  | x
|  |  | 12 | Off Level Source Type | 1 | 1 | 2 |  | Off Level Source Type | RD/CW |  |  | x
|  |  | 13 | OffLevel Source Number | 1 | 1 | 2 |  | Off Level Source Number | RD/CW |  |  | x
|  |  | 14 | Off Level Source Breaker | 1 | 1 | 2 |  | Source Breaker Bus Number 0- 15 | RD/CW |  |  | x
|  |  | 15 | Off Level | 1 | 1 | 2 |  | 0-255 | RD/CW |  |  | x
|  |  | 16 | Off Ramp Rate | 1 | 1 | 2 |  | Off Ramp Rate | RD/CW |  |  | x
|  |  | 17 | Period | 1 | 1 | 2 |  | Period | RD/CW |  |  | x
| Record Summary |  |  |  | 18 | 17 | 32
File Definition
| Record 1-256 |  |  | CBUS Output Configuration | 256 | 4352 | 8192
Total
File 13:
| File 14: System Configuration |  |  |  | Items | Registers | Bytes
|  |  |  | Controller Name Tag | 1 | 8 | 16 | 8 | 16 ASCII characters, default=Serial Number* | RD/CW |  |  | x
|  |  |  | not used | 1 | 1 | 2 | 9 | don' care | RD/CW |  |  | x
|  |  |  | not used | 1 | 1 | 2 | 10 | don' care | RD/CW |  |  | x
|  |  |  | Communication Loss Timeout Enable *1 | 1 | 1 | 2 | 11 | 0* = disable, 1 = modbus, 2=BACnet, 3=DMX | RD/CW |  |  | x
|  |  |  | Global Event Enable | 1 | 2 | 4 | 12,13 | 0 = disable, 1 = enable* - see coils 5601-5515 | RD/CW |  |  | x
|  |  |  | Global Alarm Enable | 1 | 2 | 4 | 14,15 | 0 = disable*, 1 = enable - see coils 5651-5565 | RD/CW |  |  | x
|  |  |  | Blink-to-OFF Delay | 1 | 1 | 2 |  | 120 - 1800, units = s, default = 300 | RD/CW |  |  | x
|  |  |  | Stagger Delay | 1 | 1 | 2 |  | 1* - 10, units = 0.1s | RD/CW |  |  | x
|  |  |  | Breaker Verification Delay | 1 | 1 | 2 |  | 1*- 8, units = s | RD/CW |  |  | x
|  |  |  | Enable Coil Writes | 1 | 1 | 2 |  | 9876: Enable; any other value: Disable* | RD/CW |  |  | x
|  |  |  | Front Panel Password, level 1 | 1 | 1 | 2 |  | password | RD/CW |  |  | x
|  |  |  | Front Panel Password, level 2 | 1 | 1 | 2 |  | password | RD/CW |  |  | x
|  |  |  | Front Panel Password, level 3 | 1 | 1 | 2 |  | password | RD/CW |  |  | x
|  |  |  | Front Panel Time Out | 1 | 1 | 2 |  | 1-600: units = seconds; default = 120* | RD/CW |  |  | x
|  |  |  | Sweep switch pulse width | 1 | 1 | 2 |  | 1-10: units = seconds; default = 5* | RD/CW |  |  | x
|  |  |  | Sweep switch repeat interval | 1 | 1 | 2 |  | 1-240: units = minutes; default = 120* | RD/CW |  |  | x
|  |  |  | Communication Loss Timer Setpoint | 1 | 1 | 2 |  | 1-600 seconds, default:120 seconds* | RD/CW |  |  | x
|  |  |  | FTP Password | 1 | 33 | 66 |  | 64 ASCII characters , null termination required - last character = 0, word 33 always zero, default=admin" | RD/CW |  |  | x
note *1 - msb is not validated, set to 0 by firmware
| Record Summary |  |  |  |  | 59 | 118
File Definition
| Record 1 |  |  | System Configuration | 1 | 59 | 118
Total
| File 15: Communications Configuration |  |  |  | Items | Registers | Bytes
|  |  |  | Slave RS232 Port Baud Rate | 1 | 2 | 4 |  | baud rates |  |  |  | x
|  |  |  | Slave RS232 Port Parity *1 | 1 | 1 | 2 |  | 0 = none, 1 = odd, 2 = even, default = 0* |  |  |  | x
|  |  |  | Slave RS232 Port Communications Mode *1 | 1 | 1 | 2 |  | RS232 modes |  |  |  | x
|  |  |  | Slave RS485 Port Baud Rate | 1 | 2 | 4 |  | baud rates |  |  |  | x
|  |  |  | Slave RS485 Port Parity *1 | 1 | 1 | 2 |  | 0 = none, 1 = odd, 2 = even default = 0* |  |  |  | x
|  |  |  | Slave RS485 Port Communications Mode *1 | 1 | 1 | 2 |  | RS485 modes |  |  |  | x
|  |  |  | Local IP Address | 1 | 2 | 4 |  | default = Transparent Ready TR_013 |  |  |  | x
|  |  |  | Local Subnet Mask | 1 | 2 | 4 |  | default = Transparent Ready TR_013 |  |  |  | x
|  |  |  | Local Gateway Address | 1 | 2 | 4 |  | default = Transparent Ready TR_013 |  |  |  | x
|  |  |  | TCP Connection Timeout | 1 | 1 | 2 |  | 1 - 32767, units = 1s, default = 300* |  |  |  | x
|  |  |  | TCP Read Timeout | 1 | 1 | 2 |  | 1 - 32767, units = 10 ms, default = 10* |  |  |  | x
|  |  |  | TCP Write Timeout | 1 | 1 | 2 |  | 1 - 32767, units = 10 ms, default = 10* |  |  |  | x
|  |  |  | Modbus Address | 1 | 1 | 2 |  | 1-247, default = 248* |  |  |  | x
|  |  |  | Modbus Gateway Timeout | 1 | 1 | 2 |  | 1-65535, units = seconds, default = 1s* |  |  |  | x
|  |  |  | Modbus Gateway Packet Interval | 1 | 1 | 2 |  | 1-65535, units = 10ms, default = 1 (10ms)* |  |  |  | x
|  |  |  | Modbus Gateway Character Timeout | 1 | 1 | 2 |  | 4-8, units = characters times, default = 4* |  |  |  | x
|  |  |  | BACnet MSTP Address | 1 | 1 | 2 |  | 0-127, default: 0* |  |  |  | x
|  |  |  | BACnet UDP Port | 1 | 1 | 2 |  | 0-65535, default: 47808 (0xBAC0)* |  |  |  | x
|  |  |  | BACnet BBMD IP Address | 1 | 2 | 4 |  | default: 000.000.000.000* |  |  |  | x
|  |  |  | BACnet BBMD UDP Port | 1 | 1 | 2 |  | 0-65535, default: 47808 (0xBAC0)* |  |  |  | x
|  |  |  | BACnet Device ID | 1 | 2 | 4 |  | 0-4,194,302, default: last 6 digits of serial number* |  |  |  | x
|  |  |  | BACnet Modes | 1 | 1 | 2 |  | bits 15-4: reserved, default 0* bit 3: breaker objects; 0: disable, 1: enable bit 2, control; 0: disable, 1: enable bit 1, mode; 0: BIP, 1: MSTP bit 0, enable; 0: disable BACnet, 1: enable BACnet |  |  |  | x
|  |  |  | BACnet APDU Timeout | 1 | 1 | 2 |  | 100-255, default: 200, units: s |  |  |  | x
|  |  |  | BACnet APDU Retries | 1 | 1 | 2 |  | 1-5, default: 3 |  |  |  | x
|  |  |  | BACnet BBMD Time-to-live | 1 | 1 | 2 |  | 100-65535, default: 300, units: s |  |  |  | x
|  |  |  | Cbus Area Address | 1 | 1 | 2 |  | 0-255, default =255 |  |  |  | x
|  |  |  | Cbus TCP Port | 1 | 1 | 2 |  | 1-65535, default=15000 |  |  |  | x
|  |  |  | Cbus Sync Mode | 1 | 1 | 2 |  | 0 = do nothing, 1 = get MMI status from Cbus, 3 = Input status sent to CBus, default = 0 |  |  |  | x
|  |  |  | Sntp_port_0 | 1 | 1 | 2 |  | 1-65535, default = 123* |  |  |  | x
|  |  |  | Sntp_port_1 | 1 | 1 | 2 |  | 1-65535, default = 123* |  |  |  | x
|  |  |  | Sntp_clock_upd_interval | 1 | 1 | 2 |  | 1-24, units = hours |  |  |  | x
|  |  |  | Sntp_time_server0 | 1 | 2 | 4 |  | default: 000.000.000.000 |  |  |  | x
|  |  |  | Sntp_time_server1 | 1 | 2 | 4 |  | default: 000.000.000.000 |  |  |  | x
|  |  |  | SMTP (mail) Serrver IP | 1 | 2 | 4 |  | default: 000.000.000.000 |  |  |  | x
|  |  |  | SMTP Port | 1 | 1 | 2 |  | 1-65535, default = 25 |  |  |  | x
|  |  |  | SMTP User Name | 1 | 32 | 64 |  | ASCII |  |  |  | x
|  |  |  | Mail-to designator | 1 | 5 | 10 |  | 0*: To, 1: Cc, 2: Bcc |  |  |  | x
x
note *1 - msb is not validated, set to 0 by firmware
| Record Summary |  |  |  |  | 82 | 164
NF3500
File Definition
| Record 1-2* |  |  | Communications Configuration | 1 | 82 | 164 |  | *record 2 only writes last 96 bytes - LCS use only
Total
| File 16: Clock Configuration |  |  |  | Items | Registers | Bytes
|  |  |  | Display Time Format (12/24) | 1 | 1 | 2 |  | value | RD/CW |  |  | x
|  |  |  | Time Zone Reference | 1 | 1 | 2 |  | value | RD/CW |  |  | x
|  |  |  | Latitude | 1 | 1 | 2 |  | range | RD/CW |  |  | x
|  |  |  | Longitude | 1 | 1 | 2 |  | range | RD/CW |  |  | x
|  |  |  | Daylight Saving Time Enable | 1 | 1 | 2 |  | 0=disable, 1*=US | RD/CW |  |  | x
|  |  |  | US "New" (2007-on) Rule, Start | 1 | 3 | 6 |  | week, day of week, month week: 1-5; 1=1st, 5=last day of week: 0 - 6 (0 = Sunday) month:1-12 defaults: 2, 0, 3 (2nd Sunday March) | RD/CW |  |  | x
|  |  |  | US "New" (2007-on) Rule, End | 1 | 3 | 6 |  | week, day of week, month week: 1-5; 1=1st, 5=last day of week: 0 - 6 (0 = Sunday) month:1-12 defaults: 1, 0, 11 (1st Sunday November) | RD/CW |  |  | x
| Record Summary |  |  |  |  | 11 | 22
File Definition
| Record 1 |  |  | Clock Configuration | 1 | 11 | 22 |  |  | RD/CW
Total
| File 101: Terminal Name Tags |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Terminal Name Tag | 8 | 64 | 128 |  | 16 ASCII characters per name tag |  |  |  | x
| Record Summary | [7 empty] | 8 nametags per record
File Definition
| Record 1 - 2 |  |  | Terminal Name Tag | 2 | 128 | 256 |  |  | RD/CW
Total
| File 102: Input Name Tags |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Input Name Tag | 8 | 64 | 128 |  | 16 ASCII characters per name tag |  |  |  | x
| Record Summary | [7 empty] | 8 nametags per record
File Definition
| Record 1 - 32 |  |  | Input Name Tag | 32 | 2048 | 4096 |  |  | RD/CW
Total
| File 103: Panel Name Tags |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Panel Name Tag | 8 | 64 | 128 |  | 16 ASCII characters per name tag |  |  |  | x
| Record Summary | [7 empty] | 8 nametags per record
File Definition
| Record 1- 2 |  |  | Panel Name Tag | 2 | 128 | 256 |  |  | RD/CW
Total
| File 104: Zone Name Tags |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Zone Name Tag | 8 | 64 | 128 |  | 16 ASCII characters per name tag |  |  |  | x
| Record Summary | [7 empty] | 8 nametags per record
File Definition
| Record 1- 32 |  |  | Zone Name Tag | 32 | 2048 | 4096 |  |  | RD/CW
Total
| File 105: Schedule Name Tags |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Schedule Name Tag | 8 | 64 | 128 |  | 16 ASCII characters per name tag |  |  |  | x
| Record Summary | [7 empty] | 8 nametags per record
File Definition
| Record 1 - 8 |  |  | Schedule Name Tag | 8 | 512 | 1024 |  |  | RD/CW
Total
| File 106: Period Name Tags |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Period Name Tag | 8 | 64 | 128 |  | 16 ASCII characters per name tag |  |  |  | x
| Record Summary | [7 empty] | 8 nametags per record
File Definition
| Record 1 - 128 |  |  | Period Name Tag | 128 | 8192 | 16384 |  |  | RD/CW
Total
| File 107: Special Day Name Tags |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Special Day Name Tag | 8 | 64 | 128 |  | 16 ASCII characters per name tag |  |  |  | x
| Record Summary | [7 empty] | 8 nametags per record
File Definition
| Record 1 - 12 |  |  | Special Day Name Tag | 12 | 768 | 1536 |  |  | RD/CW
Total
| File 108: Bus Name Tags |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Bus Name Tag | 8 | 64 | 128 |  | 16 ASCII characters per name tag |  |  |  | x
| Record Summary | [7 empty] | 8 nametags per record
File Definition
| Record 1- 2 |  |  | Bus Name Tag | 2 | 128 | 256 |  |  | RD/CW
Total
| File 110: Subscriber Name Tags |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Subscriber Name Tag | 8 | 64 | 128 |  | 16 ASCII characters per name tag |  |  |  | x
| Record Summary | [7 empty] | 8 nametags per record
File Definition
| Record 1-8 |  |  | Subscriber Name Tag | 8 | 512 | 1024 |  |  | RD/CW
Total
| File 112: Cbus Output Name Tags |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Cbus Output Name Tag | 8 | 64 | 128 |  | 16 ASCII characters per name tag |  |  |  | x
| Record Summary | [7 empty] | 8 nametags per record
File Definition
| Record 1- 32 |  |  | Cbus Output Name Tag | 32 | 2048 | 4096 |  |  | RD/CW
Total
File 115: Email Addresses
| File Definition | [11 empty] | x
| Record 1 |  |  | Email 'From' Address | 1 | 32 | 64 |  | 64 ASCII characters per address
| Record 2-6 |  |  | Email 'To' Address | 1 | 32 | 64 |  | 64 ASCII characters per name address
| Total | [11 empty] | x
File Definition
| Record 1- 6 |  |  | Email Addresses | 6 | 192 | 384 |  |  | RD/CW
Total
| File 118: Not used |  |  |  | Items | Registers | Bytes
Record Definition
Record Summary
File Definition
| File 119: Panel Position Name Tags |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Panel Position Name Tag | 8 | 64 | 128 |  | 16 ASCII characters per name tag |  |  |  | x
| Record Summary | [7 empty] | 8 nametags per record
File Definition
| Record 1-144 |  |  | Panel Position Name Tag | 144 | 9216 | 18432 |  | 16 ASCII characters per name tag | RD/CW
| Total | [7 empty] | 8 nametags per record
| File 207: Schedules Status |  |  |  | Items | Registers | Bytes
Record Definition
|  |  |  | Schedule Period Status | 1 | 64 | 128 |  | period status per schedule | RD |  |  | x
Record Summary
Total
| File 206 Cbus Device Type Status |  |  |  | Items | Registers | Bytes
|  |  |  | Cbus Device Type Address 0 | 1 | 12 | 24 |  |  | RD |  |  | x
|  |  |  | Cbus Device Type Address 1 | 1 | 12 | 24 |  |  | RD |  |  | x
|  |  |  | Cbus Device Type Address 2 | 1 | 12 | 24 |  |  | RD |  |  | x
|  |  |  | Cbus Device Type Address 3 | 1 | 12 | 24 |  |  | RD |  |  | x
|  |  |  | Cbus Device Type Address 4 | 1 | 12 | 24 |  |  | RD |  |  | x
|  |  |  | Cbus Device Type Address 5 | 1 | 12 | 24 |  |  | RD |  |  | x
|  |  |  | : | [8 empty] | x
|  |  |  | : | [8 empty] | x
|  |  |  | Cbus Device Type Address 254 | 1 | 12 | 24 |  |  | RD |  |  | x
|  |  |  | Cbus Device Type Address 255 | 1 | 12 | 24 |  | not valid address | RD |  |  | x
| Record Summary |  |  |  |  | 3072 | 6144
File Definition
| Record 1 |  |  | Cbus Device Type | 1 | 3072 | 6144 |  |  | RD
Total

## Data Formats
Item | Type | Location | Size | Units/Range | Default | Min | Max | NF1500PL | NF2500PL | NF3500PL
Terminal Object Parameters
Terminal Type Value | R/W |  | 1 reg. | 0 - switch | 0 | 0 | 2
1 - sensor: terminals 1-4
2 - output: terminals 9-16
Terminal Switch Type Value | R/W |  | 1 reg. | 0 - maintain N/O | 3 | 0 | 6
1 - maintained N/C
2 - maintained toggle
3 - momentary toggle
4 - momentary on
5 - momentary off
6 - dual momentary
Terminal Sensor Type Value | R/W |  | 1 reg. - terminals 1-4 only | 0 - 0-5 VDC | 0 | 0 | 2
1 - 0-10 VDC
2 - 4-20 mA
3 - 0-20 mA - not implemented
Terminal Sensor Offset | R/W |  | 2 reg.- terminals 1-4 only | A/D Sensor Calibration Offset Correction - IEEE 754 Hex Floating Point Representation | 0 | 0xFF7FFFFF | 0x7F7FFFFF
|  |  |  | Decimal Reference | 0 | -3.402E+38 | 3.402e+38
Terminal Sensor Scalar | R/W |  | 2 reg.- terminals 1-4 only | A/D Sensor Calibration Span Correction - IEEE 754 Hex Floating Point Representation | 0 | 0xFF7FFFFF | 0x7F7FFFFF
|  |  |  | Decimal Reference | 0 | -3.402E+38 | 3.402e+38
Status Output Source Type Value | R/W |  | 1 reg. | 0 - terminal | 3 | 0 | 5
1 - input
2 - schedule
3 - zone
4 - breaker
5 - remote source
Status Output Source Number | R/W |  | 1 reg. | 0 - 255 * - terminals 1-7 | *0 | 0 | 255
|  |  |  | ** - terminal 8-16 | **terminal | 0 | 255
Status Output Source Bus | R/W |  | 1 reg. | 0-15 | 0 | 0 | 15
Input Object Parameters
Input Timer Type | R/W |  | 1 reg. | 0 = no timer* | 0 | 0 | 3
1 = Timed ON
2 = OFF Delay
3 = ON Delay
Sync Source Type | R/W |  | 1 reg. | 0 - terminal | 3 | 2 | 4
1 - input
2 - schedule
3 - zone
4 - breakers
5 - remote source
Sync Source Number | R/W |  | 1 reg. | terminal: 0-15 | 0 | 0 | 15
|  |  |  | input: 0-255 | 0 | 0 | 255
|  |  |  | schedule: 0-63 | 0 | 0 | 64
|  |  |  | zone: 0-255 | 0 | 0 | 255
|  |  |  | breaker: 0-20 | 0 | 0 | 20
|  |  |  | remote source 0-63 | 0 | 0 | 64
|  |  |  | 255 - not used | 255 | 255 | 255
Sync Source Bus | R/W |  | 1 reg. | bus | 0 | 0 | 15
Sync Filter | R/W |  | 1 reg. | 0 - no sync | 0 | 0 | 3
1 - all (on/off) events
2 - on events only
3 - off events only
Sync Invert | R/W |  | 1 reg. | 0 - normal = src state | 0 | 0 | 1
1 - invert = inverted src state
Inhibit Sync Source Type | R/W |  | 1 reg. | 0 - terminal | 3 | 2 | 4
1 - input
2 - schedule
3 - zone
4 - breakers
5 - remote source
Inhibit Sync Source Number | R/W |  | 1 reg. | terminal: 0-15 | 0 | 0 | 255
input: 0-255
schedule: 0-63
zone: 0-255
breaker: 0-20
remote source 0-63
255 - not used
Inhibit Sync Source Bus | R/W |  | 1 reg. | bus | 0 | 0 | 15
Inhibit Sync Filter | R/W |  | 1 reg. | 0 - no sync | 0 | 0 | 3
1 - all (on/off) events
2 - on events only
3 - off events only
Inhibit Sync Invert | R/W |  | 1 reg | 0 - normal = src state | 0 | 0 | 1
1 - invert = inverted src state
Timer Sync Source Type | R/W |  | 1 reg. | 0 - terminal | 3 | 2 | 4
1 - input
2 - schedule
3 - zone
4 - breakers
5 - remote source
Timer Sync Source Number | R/W |  | 1 reg. | terminal: 0-15 | 0 | 0 | 255
input: 0-255
schedule: 0-63
zone: 0-255
breaker: 0-20
remote source 0-63
255 - not used
Timer Sync Source Bus | R/W |  | 1 reg. | bus | 0 | 0 | 15
Timer Sync Filter | R/W |  | 1 reg. | 0 - no sync | 0 | 0 | 3
1 - all (on/off) events
2 - on events only
3 - off events only
Timer Sync Invert | R/W |  | 1 reg. | 0 - normal = src state | 0 | 0 | 1
1 - invert = inverted src state
Scheduler Object Parameters
Schedule Status | R |  | 1 bit | 0 = Schedule OFF | 0 | 0 | 1
1 = Schedule ON
Schedule Manual | R |  | 1 bit | 0 (Always Auto) | 0 | 0 | 0
Time Period Status | R |  | 24 bits | 0 = Period Inactive | 0 | 0 | 1
(1 bit for each period, 1 - 24) |  |  |  | 1 = Period Active
Note: 32 "discrete input" bits are allocated, but only the 24 bits with the highest addresses for each period are used and valid.
Bus Parameters
Bus Model Number | R |  | 1 reg. | 0 = no bus | 0 | 0 | 14
1 = 6 position R
2 = 6 position L
3 = 9 position R
4 = 9 position L
5 = 12 position R (NF12SBR)
6 = 12 position L (NF12SBL)
7 = 15 position R (NF15SBR)
8 = 15 position L (NF15SBL)
9 = 18 position R (NF18SBR)
10 = 18 position L (NF18SBL)
11 = 21 position R (NF21SBR)
12 = 21 position L (NF21SBL)
13 = 24 position R (NF24SBR)
14 = 24 position L (NF24SBL)
Bus Firmware Version | R |  | 1 reg. | MS byte = version | 1 | 1 | 1
|  |  |  | LS byte = revision | 0 | 0 | 0
Bus Panel | R/W |  | 1 reg. | 0 - 15 | Default: | 0 | 15
0 = bus0,bus1
1 = bus2,bus3
2 = bus4,bus5
3 = bus6,bus7
4 = bus8,bus9
5 = bus10,bus11
6 = bus12,bus13
7 = bus14,bus15
Breaker Blink Type |  |  |  | 0 = none | 0 | 0 | 6
1 = single
2 = double
3 = triple
4 = delay only
5 = sentry
6 = sentry w/repeat
Breaker Type
|  |  |  | 0 = Not Present | 0 | 0 | 3
1 = 1 pole
2 = 2 pole
3 = 3 pole
Zone Object Parameters
Zone Logic Type | R/W |  | 1 reg. | 0 = OR Logic* | 0 | 0 | 5
1 = AND
2 = last event
3 = XOR
4 = Custom Logic
5 = Truth Table Logic
Zone Custom Logic Truth Table | R/W |  | 1 reg. | a 4 variable (16 row) truth table is specified as follows: | 0x0 | 0x0 | 0xFFFF
A B C D f
0 0 0 0 a
0 0 0 1 b
:
1 1 1 1 p
where the 16 bit value is specfied as:
ponmlkjihgfedcba
Zone Last Event |  |  | 1 reg. | bit 15: source 0 ON filter: 1: respond to ON events | 0xEEEE | 0 | 0xFFFF
bit 14: source 0 OFF filter: 1: respond to OFF events
bit 13: source 0 ON transition, set zone state: 0: OFF, 1:ON
bit 12: source 0 OFF transition, set zone state: 0: OFF, 1:ON
bit 11 - 8: source 1
bit 7 - 4: source 2
bit 3 - 0: source 3
Zone Comms Loss Action | R/W |  | 1 reg. | 0 = none
|  |  |  | 1 = run /release | 0 | 0 | 4
2 = last state
3 = on
4 = off
Zone Comms Restore Action | R/W |  | 1 reg. | 0 = none
|  |  |  | 1 = run /release | 0 | 0 | 4
2 = last state
3 = on
4 = off
Zone Action/Priority | R/W |  | 1 reg. | 0 = normal | 0 | 0 | 1
1 = priority OFF
2 = priority ON
Zone Source Pointer | R/W |  | 1 reg. | Type: | 255 | 0 | 255
4 Source Pointers - each use 5 registers |  |  |  | 0 - terminal
1 - input
2 - schedule
3 - zone
4 - breakers
5 - remote source
255 - not used
| R/W |  | 1 reg. | Number:
|  |  |  | terminal: 0-15 | 0 | 0 | 255
input: 0-255
schedule: 0-63
zone: 0-255
breaker: 0-20
remote source 0-63
255 - not used
| R/W |  | 1 reg. | Bus:
|  |  |  | bus: 0-15 | 0 | 0 | 15
| R/W |  | 1 reg. | Operator:
0 - AND
1 - OR
2 - XOR
3 - NAND
4 - NOR
5 - XNOR
| R/W |  | 1 reg. | Polarity: | 0 | 0 | 1
1 - normal
0 - inverted
Zone Member List Bus | R/W |  | 32 reg. | (See Table)
Each zone, 1 – 255, is comprised of 64 bytes, each 32 bit element being a bit map of breakers: |  |  |  |  | 0 | 0 | 0x001FFFFF
NNNNNNNN 22222111 11111110 00000000 AAAAAAAA 43210987 65432109 87654321
00000000 00000000 00000000 00000001
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
00000000 00000000 00000000 00000000
Note: Illustration shows a group member list with only breaker 1, bus address 0 included. Default value is all 0’s.
System/Misc Configuration
Firmware Version (DLF compatible format) | R |  | 1 reg. - DLF use only | Firmware Version read from G4 - valid range 0-63 | 0 | 0 | 63
Firmware Revision (DLF compatible format) | R |  | 1 reg. - DLF use only | (Firmware Revision read from G4) * 10 - valid range 0-99 | 0 | 0 | 99
Blink Pulse Duration | R/W |  | 1 reg. | 2 to 100 (5*) | 5 | 2 | 100
Unsigned 16 bit integer
Scaling: 1 count = 0.1 sec.
Blink-to-OFF Delay | R/W |  | 1 reg. | Limited to 120 to 1800 seconds (300*) | 300 | 120 | 1800
Unsigned 16 bit integer
Stagger Delay | R/W |  | 1 reg. | 1* - 10 | 1 | 1 | 10
Unsigned 16 bit integer
Scaling: 1 count = 0.1 sec.
Breaker Verification Delay | R/W |  | 1 reg. | 1* - 8 | 1 | 1 | 8
Unsigned 16 bit integer
Scaling: 1 count = 1 sec.
Manufacturing Information | R/W |  | 8 reg. | To Be Determined by MFG.
Front Panel Password | R/W |  | 1 reg. | 0 – 9999, with 0000 = Disabled | 0 | 0 | 9999
Front Panel Disable Timeout (comms inactivity) | R/W |  | 1 reg. | Limited to 1 to 120 min | 5 | 1 | 120
Unsigned 16 bit integer
Self-Test Bitmap | RO |  | 1 reg. | bit 15: enable download
bit 14: enter download
bit 13: DL module running
bit 12: APP module running
bit 11: DL module valid
bit 10: APP module valid
bit 9: N/A
bit 8: production mode enabled
bit 7: command interface enabled
bit 6: configuration mode enabled
bit 5: front panel disabled
bit 4: "internal" halt mode enabled
bit 3: real-time clock running
bit 2: last reset cause: 1: soft, 0: hard
bit 1: C-Bus device
bit 0: N/A
Hardware Peripheral Status | RO |  | 1 reg. | bit 15: LCD module | 0 | 0 | 65535
bit 14: NVSRAM
bit 13: RTC
bit 12: DDRAM
bit 11:
bit 10: Ethernet switch
bit 9: Flash Memory - 0xC0000000
bit 8: Flash Memory -0xC1000000
bit 7:
bit 6:
bit 5:
bit 4: AD converter
bit 3:
bit 2:
bit 1:
bit 0:
0: present/functional
1: not present/not functional
Key Press Status | RO |  | 1 reg. | bit 3: + enter
bit 2: - minus
bit 1: > forward
bit 0: < backward
Device ID | RO |  | 1 reg. | NF500: 15156
Option ID | RO |  | 1 reg. | This register is available if required to differentiate devices having the same device ID. As of the initial release of the NF1000, this register does not contain meaningful information.
Clock/Calendar Parameters
Calculated Day of Week | R |  | 1 reg. | Code: | 0 | 0 | 6
0 = Sunday
1 = Monday
2 = Tuesday
3 = Wednesday
4 = Thursday
5 = Friday
6 = Saturday
Calculated Week of Month | R |  | 1 reg. | Bitmapped: | 0 | 0 | 48
bit 0:1st week
bit 1: 2nd week
bit 2: 3rd week
bit 3: 4th week
bit 4: 5th week
bit 5: last week
bit 6:bit 4: last week
bti 6 bit 5: last week
Calculated DST Month | R |  | 1 reg. | Month = 1 - 12 | 1 | 1 | 12
Calculated DST Day | R |  | 1 reg. | Day = 1 - 31 | 1 | 1 | 32
Calculated Sunrise/Sunset Time Hour (Today) | R |  | 1 reg. | Hour = 0 - 23 | 0 | 0 | 23
Calculated Sunrise/Sunset Time Minutes (Today) | R |  | 1 reg. | Minutes = 0 - 59 | 0 | 0 | 59
Compressed Local Date/Time | R/W |  | 3 reg. | r1 (MS Byte) : Month = 1 - 12
r1 (LS Byte) : Day = 1 - 31
r2 (MS Byte): Year = 0 - 99
r2 (LS Byte): Hour = 0 - 23
r3 (MS byte): Minutes = 0 - 59
r3 (LS Byte): Seconds = 0 - 59
Expanded Local Date/Time | R/W |  | 6 reg. | r1: Month = 1 - 12
r2 : Day = 1 - 31
r3: Year = 2000-2099
r4: Hour = 0 - 23
r5: Minutes = 0 - 59
r6: Seconds = 0 - 59
Display Time 12/24 Format | R/W |  | 1 reg. | 12 = 12 hr (AM/PM)* | 12 | 12 | 24
24 = 24 hr
Time Zone Reference | R/W |  | 1 reg. | -48 to 48 | -24 | -48 | 48
(Offset from GMT) |  |  | Signed 16-bit integer
|  |  | 48 | GMT + 12:00
|  |  | 44 | GMT + 11:00
|  |  | 40 | GMT + 10:00
|  |  | 38 | GMT + 9:30
|  |  | 36 | GMT + 9:00
|  |  | 32 | GMT + 8:00
|  |  | 28 | GMT + 7:00
|  |  | 24 | GMT + 6:00
|  |  | 22 | GMT + 5:30
|  |  | 20 | GMT + 5:00
|  |  | 18 | GMT + 4:30
|  |  | 16 | GMT + 4:00
|  |  | 14 | GMT + 3:30
|  |  | 12 | GMT + 3:00
|  |  | 8 | GMT + 2:00
|  |  | 4 | GMT + 1:00
|  |  | 0 | GMT
|  |  | -4 | GMT - 1:00
|  |  | -8 | GMT - 2:00
|  |  | -12 | GMT - 3:00
|  |  | -14 | GMT - 3:30 (Newfoundland)
|  |  | -16 | GMT - 4:00 (Atlantic)
|  |  | -20 | GMT - 5:00 (Eastern)
|  |  | -24 | GMT - 6:00 (Central)
|  |  | -28 | GMT - 7:00 (Mountain)
|  |  | -32 | GMT - 8:00 (Pacific)
|  |  | -36 | GMT - 9:00 (Alaska)
|  |  | -40 | GMT - 10:00 (Hawaii)
|  |  | -44 | GMT - 11:00
|  |  | -48 | GMT - 12:00
Latitude (North-South) | R/W |  | 1 reg. | - 90 to + 90 | 36 | -90 | 90
Signed 16-bit integer
Scaling = 1 Degree / Count
default = 36 (N)
Longitude (East-West) | R/W |  | 1 reg. | - 180 (West) to + 180 (East) | -86 | -180 | 180
Signed 16-bit integer
Scaling = 1 Degree / Count
default = -86
Communications Parameters
RS232 Baud Rate | R/W |  | 2 reg. | 4800 | 38400 | 4800 | 115200
9600****
19200
38400*
76800
115200
RS232 Communications Mode | R/W |  | 1 reg. | 1 = Modbus Agile* | 1 | 1 | 6
2 = ASCII
3 = RTU
4 = C-Bus****
5 = Modbus TCP passthrough to RS232
6 = Modbus RS232 passthrough to RS485
RS485 Baud Rate | R/W |  | 2 reg. | 4800 | 38400 | 4800 | 250000
9600
19200
38400*
76800**
115200
250000***
RS485 Communications Mode | R/W |  | 1 reg. | 1 = Modbus Agile* | 1 | 1 | 7
2 = ASCII
3 = RTU
4 = DMX***
5 = BACnet**
6 = Modbus RS232 passthrough to RS485
7 = Modbus TCP passthrough to RS485
IP Address Defaults - TR_013 | R/W |  | 2 reg. |  | 0.0.0.1 | 255.255.255.254 | 0.0.0.0
IP Adress |  |  | 1st reg hi word, 2nd reg lo word | Default = 0.0.0.0
Subnet Address |  |  | 1st reg hi word, 2nd reg lo word | Default = 255.255.255.0 - Class C Ip
Gateway Address |  |  | 1st reg hi word, 2nd reg lo word | Default = 0.0.0.0 - no routing
External Source Global Control Parameters
External Source Value | R |  | 2 bit pair | First bit = State
0 = OFF
1 = ON
Second Bit = Manual Flag
0 = Auto
1 = Manual
External Source Default Active | R |  | 1 bit | 1 = Default Active
External Source Service State | R |  | 1 bit | 0 = In Service
1 = Out of Service
External Source Default Time-Out Value | R |  | 1 reg. | 0 - 1800 (10*)
Unsigned 16-bit integer
Scaling = 1 second / count
External Source xx IP Address Table | R/W |  | 2 reg. | r1 (MS byte) = ww
r1 (LS Byte) = xx
r2 (MS byte) = yy
r2 (LS byte) = zz
ww.xx.yy.zz = IP addr.
External Reference xx Register Selector | R/W |  | 1 reg. | Range = 00001 to 19999
(Corresponds to panel at IP address) |  |  |  | Unsigned 16 bit integer
Where MSB/LSB =
coil/input #
External Source Default Value | R/W |  | 1 reg. | 0 = No Change on update failure*
(1 for each Ext. Source) |  |  |  | 1 = Automatic ON on update failure
2 = Automatic OFF on update failure
3 = Manual OFF on update failure
External Source Number of Time-Outs | R/W |  | 1 reg. | 0 - 65532
(1 for each External Source) |  |  |  | Unsigned 16-bit integer
External Source Number of Retries | R/W |  | 1 reg. | 0 - 65532
(1 for each External Source) |  |  |  | Unsigned 16-bit integer
External Source Number of Errors | R/W |  | 1 reg. | 0 - 65532
(1 for each External Source) |  |  |  | Unsigned 16-bit integer
External Source Default Time-Out Duration | R/W |  | 1 reg. | 0 - 1800 (10*)
Unsigned 16-bit integer
Scaling = 1 second / count
Period Parameters
Start Time, Hours | R/W |  | .5 reg. | MS byte = Code: | 0 | 0 | 25
0 - 23 = Hour
24 = Sunrise
25 = Sunset
Start Time, Minutes | R/W |  | .5 reg. | LS Byte = Minutes | 0 | 0 | 59
Range = 0 - 59
Start_Offset, Minutes-from Sunrise or Sunset | R/W |  | 1 reg. | -120 to 120 minutes
End Time, Hours | R/W |  | .5 reg. | MS byte = Code: | 0 | 0 | 25
0 - 23 = Hour
24 = Sunrise
25 = Sunset
End Time, Minutes | R/W |  | .5 reg. | LS Byte = Minutes | 0 | 0 | 59
Range = 0 - 59
End Offset, Minutes-from Sunrise or Sunset | R/W |  | 1 reg. | -240 to 240 minutes
Day of Week | R/W |  | 1 reg. | bitmap: bit 0 - Sunday | 0 | 0 | 127
bit 1 - Monday
bit 2 - Tuesday
bit 3 - Wednesday
bit 4 - Thursday
bit 5 - Friday
bit 6 - Saturday
Special Days | R/W |  | 6 reg. | bitmap: bit 0 - Special; Day 1 | 0 | 0 | 2^95
:
bit 95 - Special Day 96
Schedule Parameters
Periods | R/W |  | 64 reg. | bitmap: bit 0 - Period 1 | 0 | 0 | 2^1024
:
bit 1023 - Period 1024
Schedule Status
Output Status | R/W |  | 8 reg. | bitmap: bit 0 - Schedule 1 | 0 | 0 | 2^64
:
bit 63 - Period 64
Period Status per Schedule | R/W |  | 64 reg. | Every 32 bits is a bitmap. MSbit is 1 LSBit is 32 and repeat. | 0 | 0 | 2^1024
(period 32) 00000000000000000000000000000001 (period 1)
(period 64) 00000000000000000000000000000001 (period 33)
….
Special Condition Record Fields
Special Day x: Repeat Type | R/W |  | 1 reg. | 0 = holiday
|  |  |  | 1 = Repeat every week forever | 0 | 0 | 12
2 = Repeat every week with qualification
3 = Repeat every month by date
4 = Repeat every month by date with qualification
5 = Repeat every month by day
6 = Repeat every month by day with qualification
7 = Repeat every year by date
8 = Repeat every year by date with qualification
9 = Repeat every year by day
10 = Repeat every year by day with qualification
11 = Repeat every nn days
12 = Repeat every nn days with end date
Special Day x: Start Day | R/W |  | 1 reg. | 1-31 | 1 | 1 | 31
Special Day x: Start Month | R/W |  | 1 reg. | 1 - 12 (1 = January) | 1 | 1 | 12
Special Day x: Start Year | R/W |  | 1 reg. | 0 - 99 (Starting_Year + 2000) | 1 | 0 | 199
Special Day x: End Day | R/W |  | 1 reg. | 1-31 | 1 | 1 | 31
Special Day x: End Month | R/W |  | 1 reg. | 1 - 12 (1 = January) | 1 | 1 | 12
Special Day x: End Year | R/W |  | 1 reg. | 0 - 99 (Ending_Year + 2000) | 1 | 1 | 199
Special Day x: Day of Week | R/W |  | 1 reg. | 0 - 6 (0 = Sunday) | 1 | 0 | 6
Special Day x: Week of Month | R/W |  | 1 reg. | 1 = 1st week | 1 | 1 | 5
2 = 2nd week
3 = 3rd week
4 = 4th week
5= 5th week
Special Day x: Month of Year | R/W |  | 1 reg. | 1 - 12 (1 = January) | 1 | 1 | 12
Special Day x: Day of Month | R/W |  | 1 reg. | 1-31 | 1 | 1 | 31
Special Day x: Thru_Month | R/W |  | 1 reg. | 1 - 12 (1 = January) | 1 | 1 | 12
Special Day x: Thru_Day | R/W |  | 1 reg. | 1-31 | 1 | 1 | 31
Special Day x: Priority | R/W |  | 1 reg. | 0 - lowest priority | 1 | 0 | 3
2 - highest priority
Special Day x: Duration | R/W |  | 1 reg. | 1 - 365 days fro repeat types | 1 | 1 | 365
1 - 7 days for holidays except New Years Eve
1 - for New Years Eve
Special Day x: Repeat Interval | R/W |  | 1 reg. | 1-99 | 1 | 1 | 99
Special Day x: Holiday | R/W |  | 1 reg. | 0-13 | 0 | 0 | 13
0 - New Year's Day
1 - Martin Luther King Jr. Day
2 - Good Friday
3 - Memorial Day
4 - Fourth of July
5 - Labor Day
6 - Columbus Day
7 - Election Day
8 - Veterans' Day
9 - Thanksgiving
10 - Black Friday
11 - Christmas Eve
12 - Christmas Day
13 - New Year's Eve
Cbus Outputs Parameters
Source Type | R/W |  | 1 reg. | 0 - terminal | 255 | 0 | 255
1 - input
2 - schedule
3 - zone
4 - breaker
5 - remote source
6 - periodic
255 - not used
Source Number | R/W |  | 1 reg. | terminal: 0-15 | 0 | 0 | 255
input: 0-255
schedule: 0-63
zone: 0-255
breaker: 0-20
remote source 0-63
255 - not used
Application Number | R/W |  | 1 reg. | 48 - 95: Lighting Applications | 56 | 48 | 203
202: Trigger Application:
203: Enable Application:
[5 empty] | 0 | 0 | 255
Group Number | R/W |  | 1 reg. | 0-255: lighting group
0-255: trigger group
0-255: enable network variable
On Level Source Type | R/W |  | 1 reg. | 0 - terminal | 255 | 0 | 7
1 - input
7 - this object
255-not used
On Level Source Number | R/W |  | 1 reg. | terminal: 0-15 | 0 | 0 | 255
input: 0-255
schedule: 0-63
zone: 0-255
breaker: 0-20
remote source 0-63
255 - not used
On Ramp Rate | R/W |  | 1 reg. | 0 - seconds | 0 | 0 | 1020
4 - seconds
8 - seconds
12 - seconds
20 - seconds
30 - seconds
40 - seconds
60 - seconds
90 - seconds
120 - seconds
180 - seconds
300 - seconds
420 - seconds
600 - seconds
900 - seconds
1020 - seconds
Off Level Source Type | R/W |  | 1 reg. | 0 - terminal | 255 | 0 | 7
1 - input
7 - this object
255- not used
[5 empty] | 0 | 0 | 255
Off Level Source Number | R/W |  | 1 reg. | terminal: 0-15
input: 0-255
schedule: 0-63
zone: 0-255
breaker: 0-20
remote source 0-63
255 - not used
Off Ramp Rate | R/W |  | 1 reg. | 0 - seconds
4 - seconds
8 - seconds
12 - seconds
20 - seconds
30 - seconds
40 - seconds
60 - seconds
90 - seconds
120 - seconds
180 - seconds
300 - seconds
420 - seconds
600 - seconds
900 - seconds
1020 - seconds
Period | R/W |  | 1 reg. | 4 - seconds | 4 | 600 | 60
8 - seconds
12 - seconds
20 - seconds
30 - seconds
40 - seconds
60 - seconds
90 - seconds
120 - seconds
180 - seconds
300 - seconds
420 - seconds
600 - seconds
Subscriber File Record Fields
Publisher IP Address | R/W |  | 4 bytes | xxx.xxx.xxx.xxx, where 1£ xxx£ 255
Publisher Unit ID | R/W |  | 1 byte | 1-247; corresponds to publisher Modbus address
Subscription Number | R/W |  | 1 byte | = external source number = (record number + 1)/ 2
Type | R/W |  | 1 byte | 0: coil/input, 1: register
Length | R/W |  | 1 byte | always 1
Subscribe-to Starting Address | R/W |  | 2 bytes | coil/input or register address
Publish-to Starting Address | R/W |  | 2 bytes | coil/input or register address
Heartbeat Interval | R/W |  | 2 bytes | 60-7200 seconds; default: 300 s
Publisher Timeout | R/W |  | 2 bytes | heartbeat interval x 3
Minimum Interval | R/W |  | 2 bytes | always 0: not implemented in v3.00
Periodic Publish Interval | R/W |  | 2 bytes | always 0: not implemented in v3.00
Publisher File Number | R/W |  | 2 bytes | always 10
Default Value | R/W |  | 2 bytes | the default value is determined by both records, state and manual flag, comprising a subscription: state = 0; man flag = 0: OFF w/blink state = 0, man flag = 1: OFF (no blink) state = 1, man flag = 0: ON (w/blink ) state = 1, man flag = 0: ON (no blink) state = 0xFFF, man flag = 0xFFF: Last state
Event Log Record Fields
Reserved | R |  | 1
Event Identifier
Register/Coil # of Event | R |  | 1 | coil / register corresponding to:
Schedule Output Status
Input Object State
Latched Input State
Group State
Group Override Enable
Group Override Type
Non-Responding Breaker State
Breaker Present
Group Override Time-Out Enable
Communications Time-Out Active
Learn Mode
Halt Mode
Timer Inhibit
Bus Present
Front Panel Disable
External Source
Alarm Type | R |  | 0.5 | 60 = status change to ON
61 = status change to OFF
Reserved | R |  | 0.5
Entry Type | R |  | 1 | one shot
Reserved | R |  | 1
Event Time/Date | R |  | 4 | time/date
Correlation Sequence Number | R
Alarm Setup Record Fields
Alarm Type | R/W |  | 0.5 | 60 = status change to ON
61 = status change to OFF
10 = status > pickup value
20 = status < pickup value
Alarm Level | R/W |  | 0.5 | alarm level
Alarm Enable/Disable | R/W |  | 0.5 | 0 = disable, 1 = enable
Alarm Priority | R/W |  | 0.5 | 0 - 5
Alarm Name | R/W |  | 8 | 16 ASCII characters
Alarm Pickup Level | R/W |  | 1 | pickup level
Alarm Dropout Level | R/W |  | 1 | dropout level
Alarm Log Record Fields
Reserved | R |  | 1
Event Identifier
Test Register | R |  | 1
Alarm Type | R |  | 0.5 | 60 = status change to ON
61 = status change to OFF
10 = status > pickup value
20 = status < pickup value
Alarm Level | R |  | 0.5 | alarm level
Entry Type | R |  | 1 | pickup
dropout
one-shot
unknown
Reserved | R |  | 1
Event Time/Date | R |  | 4 | time/date
Reserved | R |  | 2
Correlation Sequence Number | R |  | 1
Result Code Description | Description
Result Code Description
Command Successful | 0
Illegal Transition | 14
Illegal Record Size | 15
Illegal File Command | 16
Insufficient Memory | 17
Illegal File Number | 42
Undefined Command | 81
Command Has Undefined or Illegal Parameters | 82
Illegal Record Request | 107
Illegal Record Count | 125
Protected Mode Not Enabled | 200
Timeout, Command Not Executed | 201
Invalid Password, Command Not Executed | 202
Configuration Mode Open Error | 204
Mode Not Enabled | 205
Terminal Object Configuration Error | 1001
Input Object Configuration Error | 1002
Panel Object Configuration Error | 1003
Zone Object Configuration Error | 1004
Schedule Object Configuration Error | 1005
Periods Object Configuration Error | 1006
Special Days Object Configuration Error | 1007
Bus/Breaker Configuration Error | 1008
Subscriber Object Configuration Error | 1009
N/A | 1010
N/A | 1011
Cbus Output Object Configuration Error | 1012
N/A | 1013
System Object Configuration Error | 1014
Communications Object Configuration Error | 1015
Clock Object Configuration Error | 1016
Email Errors
No Attempt, No Error | 0 | Default value till event/alarm triggers email
No Error | 1
Mail Port Connection Mailed | 2
Authentication Server Mailed | 3
Invalid Server | 4
Invalid From Address Server | 5
Invalid To Address Server | 6
Invalid Message Data | 7
Invalid IP | 8
Invalid From Address | 9
Invalid To Address | 10

## Control Bus Numbering
Control Bus Numbering
Control bus addresses are set locally at each control bus. A power supply, or a slave address selector must be present in each panel. The slave address selector has eight address settings, 0 to 7, which sets the address of the first control bus in the panel. Since more than one control bus may be added to a panel, there could be up to 4 addresses for each panel, for a total of 16 control bus addresses. Note that slave address selector address 0 may only be used if the controller and power supply are remotely mounted.
The 16 control bus addresses are identified by a one letter designation, such as A, B, C, D,.....,P. The control bus designation is based on two factors: The Slave Address Selector setting, and how many control buses are in a panel. Refer to the instruction bulletin for slave address selector mounting.
|  | Control Bus Address Designation | [7 empty] | Two Control Bus Numbering - Master and Slave Panel Example
[9 empty] | 30 Circuit Master Panel | [6 empty] | 30 Circuit Slave Panel #1
[9 empty] | Utilizing 2 - 12 circuit control buses | [6 empty] | Utilizing 2 - 12 circuit control buses
[10 empty] | BUS POSITION |  |  | BUS POSITION |  |  |  | BUS POSITION |  |  | BUS POSITION
[11 empty] | Ckt Number | Ckt Number | [5 empty] | Ckt Number | Ckt Number
[9 empty] | NF12SBLG3 (A) | P | 1 | 2 | C | NF12SBRG3 (B) | P= Power Supply | NF12SBLG3 (C) |  | 1 | 2 |  | NF12SBRG3 (D)
[10 empty] | P | 3 | 4 | C |  | C= Controller |  |  | 3 | 4
[10 empty] | P | 5 | 6 | C |  |  |  |  | 5 | 6
[10 empty] | 1 | 7 | 8 | 1 |  |  |  | 1 | 7 | 8 | 1
[10 empty] | 2 | 9 | 10 | 2 |  |  |  | 2 | 9 | 10 | 2
[10 empty] | 3 | 11 | 12 | 3 |  |  |  | 3 | 11 | 12 | 3
[10 empty] | 4 | 13 | 14 | 4 |  |  |  | 4 | 13 | 14 | 4
[10 empty] | 5 | 15 | 16 | 5 |  |  |  | 5 | 15 | 16 | 5
[10 empty] | 6 | 17 | 18 | 6 |  |  |  | 6 | 17 | 18 | 6
[10 empty] | 7 | 19 | 20 | 7 |  |  |  | 7 | 19 | 20 | 7
[10 empty] | 8 | 21 | 22 | 8 |  |  |  | 8 | 21 | 22 | 8
[10 empty] | 9 | 23 | 24 | 9 |  |  |  | 9 | 23 | 24 | 9
[10 empty] | 10 | 25 | 26 | 10 |  |  |  | 10 | 25 | 26 | 10
[10 empty] | 11 | 27 | 28 | 11 |  |  |  | 11 | 27 | 28 | 11
[10 empty] | 12 | 29 | 30 | 12 |  |  |  | 12 | 29 | 30 | 12
Control Bus Numbering – Four Control Bus Panelboards
The 54 cuircuit and 66 circuit panels with more than two buses requires some control buses to be mounted differently than in other standard panels. For the master panel, the normally left-mounted control bus "C" and normally right mounted control bus "D" are rotated and mounted upside-down at the bottom of the panel. The "A" and "B" bus will not change. The Slave Address Selector or Power Supply will continue to always assumed to be the “A” bus and the bus with the Wiring Harness or Controller will continue to always assumed to be the “B” bus. Note the 84 circuit panel with more than two buses does not follow the upside-down mounted control bus pattern. See the example drawings below along with determining the modbus register.
Individual Panels with Four Control Buses Numbering
54 Circuit Master Panel | [8 empty] | 54 Circuit Slave Panel #1
Utilizing 4 - 12 circuit control buses | [8 empty] | Utilizing 4 - 12 circuit control buses
| BUS POSITION |  |  | BUS POSITION | [5 empty] | BUS POSITION |  |  | BUS POSITION
|  | Ckt Number | Ckt Number | [7 empty] | Ckt Number | Ckt Number
NF12SBLG3 (A) | P | 1 | 2 | C | NF12SBRG3 (B) |  | P= Power Supply |  | NF12SBLG3 (E) |  | 1 | 2 |  | NF12SBRG3 (F)
| P | 3 | 4 | C |  |  | C= Controller |  |  |  | 3 | 4
| P | 5 | 6 | C |  |  | X= Slave Address selector |  |  |  | 5 | 6
| 1 | 7 | 8 | 1 | [5 empty] | 1 | 7 | 8 | 1
| 2 | 9 | 10 | 2 | [5 empty] | 2 | 9 | 10 | 2
| 3 | 11 | 12 | 3 | [5 empty] | 3 | 11 | 12 | 3
| 4 | 13 | 14 | 4 | [5 empty] | 4 | 13 | 14 | 4
| 5 | 15 | 16 | 5 | [5 empty] | 5 | 15 | 16 | 5
| 6 | 17 | 18 | 6 | [5 empty] | 6 | 17 | 18 | 6
| 7 | 19 | 20 | 7 | [5 empty] | 7 | 19 | 20 | 7
| 8 | 21 | 22 | 8 | [5 empty] | 8 | 21 | 22 | 8
| 9 | 23 | 24 | 9 | [5 empty] | 9 | 23 | 24 | 9
| 10 | 25 | 26 | 10 | [5 empty] | 10 | 25 | 26 | 10
| 11 | 27 | 28 | 11 | [5 empty] | 11 | 27 | 28 | 11
| 12 | 29 | 30 | 12 | [5 empty] | 12 | 29 | 30 | 12
NF12SBRG3 (D) | 12 | 31 | 32 | 12 | NF12SBLG3 (C) |  |  |  | NF12SBRG3 (H) | 12 | 31 | 32 | 12 | NF12SBLG3 (G)
| 11 | 33 | 34 | 11 | [5 empty] | 11 | 33 | 34 | 11
| 10 | 35 | 36 | 10 |  | Example: |  |  |  | 10 | 35 | 36 | 10 |  | Example:
| 9 | 37 | 38 | 9 |  | Circuit Number 38 |  |  |  | 9 | 37 | 38 | 9 |  | Circuit Number 38
| 8 | 39 | 40 | 8 |  | Bus C |  |  |  | 8 | 39 | 40 | 8 |  | Bus G
| 7 | 41 | 42 | 7 |  | Bus Position 9 |  |  |  | 7 | 41 | 42 | 7 |  | Bus Position 9
| 6 | 43 | 44 | 6 |  | Direct Breaker Control Manual Coil Register 06073 |  |  |  | 6 | 43 | 44 | 6 |  | Direct Breaker Control Manual Coil Register 06201
| 5 | 45 | 46 | 5 | [5 empty] | 5 | 45 | 46 | 5
| 4 | 47 | 48 | 4 | [5 empty] | 4 | 47 | 48 | 4
| 3 | 49 | 50 | 3 | [5 empty] | 3 | 49 | 50 | 3
| 2 | 51 | 52 | 2 | [5 empty] | 2 | 51 | 52 | 2
| 1 | 53 | 54 | 1 | [5 empty] | 1 | 53 | 54 | 1
|  |  |  | X | [8 empty] | X
|  |  |  | X | [8 empty] | X
|  |  |  | X | [8 empty] | X
66 Circuit Master Panel - Top Fed | [8 empty] | 66 Circuit Slave Panel #1 - Top Fed
Utilizing 4 - 12 circuit control buses | [8 empty] | Utilizing 4 - 12 circuit control buses
| BUS POSITION |  |  | BUS POSITION | [5 empty] | BUS POSITION |  |  | BUS POSITION
|  | Ckt Number | Ckt Number | [7 empty] | Ckt Number | Ckt Number
NF12SBLG3 (A) | P | 1 | 2 | C | NF12SBRG3 (B) |  | P= Power Supply |  | NF12SBLG3 (E) |  | 1 | 2 |  | NF12SBRG3 (F)
| P | 3 | 4 | C |  |  | C= Controller |  |  |  | 3 | 4
| P | 5 | 6 | C |  |  | X= Slave Address selector |  |  |  | 5 | 6
| 1 | 7 | 8 | 1 |  |  | N=Non-controllable Breaker |  |  | 1 | 7 | 8 | 1
| 2 | 9 | 10 | 2 | [5 empty] | 2 | 9 | 10 | 2
| 3 | 11 | 12 | 3 | [5 empty] | 3 | 11 | 12 | 3
| 4 | 13 | 14 | 4 | [5 empty] | 4 | 13 | 14 | 4
| 5 | 15 | 16 | 5 | [5 empty] | 5 | 15 | 16 | 5
| 6 | 17 | 18 | 6 | [5 empty] | 6 | 17 | 18 | 6
| 7 | 19 | 20 | 7 | [5 empty] | 7 | 19 | 20 | 7
| 8 | 21 | 22 | 8 | [5 empty] | 8 | 21 | 22 | 8
| 9 | 23 | 24 | 9 | [5 empty] | 9 | 23 | 24 | 9
| 10 | 25 | 26 | 10 | [5 empty] | 10 | 25 | 26 | 10
| 11 | 27 | 28 | 11 | [5 empty] | 11 | 27 | 28 | 11
| 12 | 29 | 30 | 12 | [5 empty] | 12 | 29 | 30 | 12
NF12SBRG3 (D) | 12 | 31 | 32 | 12 | NF12SBLG3 (C) |  |  |  | NF12SBRG3 (H) | 12 | 31 | 32 | 12 | NF12SBLG3 (G)
| 11 | 33 | 34 | 11 | [5 empty] | 11 | 33 | 34 | 11
| 10 | 35 | 36 | 10 |  | Example: |  |  |  | 10 | 35 | 36 | 10 |  | Example:
| 9 | 37 | 38 | 9 |  | Circuit Number 38 |  |  |  | 9 | 37 | 38 | 9 |  | Circuit Number 38
| 8 | 39 | 40 | 8 |  | Bus C |  |  |  | 8 | 39 | 40 | 8 |  | Bus G
| 7 | 41 | 42 | 7 |  | Bus Position 9 |  |  |  | 7 | 41 | 42 | 7 |  | Bus Position 9
| 6 | 43 | 44 | 6 |  | Direct Breaker Control Manual Coil Register 06073 |  |  |  | 6 | 43 | 44 | 6 |  | Direct Breaker Control Manual Coil Register 06201
| 5 | 45 | 46 | 5 | [5 empty] | 5 | 45 | 46 | 5
| 4 | 47 | 48 | 4 | [5 empty] | 4 | 47 | 48 | 4
| 3 | 49 | 50 | 3 | [5 empty] | 3 | 49 | 50 | 3
| 2 | 51 | 52 | 2 | [5 empty] | 2 | 51 | 52 | 2
| 1 | 53 | 54 | 1 | [5 empty] | 1 | 53 | 54 | 1
|  | PHYSICAL GAP |  | x | [6 empty] | PHYSICAL GAP |  | x
|  |  |  | x | [8 empty] | x
|  |  |  | x | [8 empty] | x
| N | 55 | 56 | N | [5 empty] | N | 55 | 56 | N
| N | 57 | 58 | N | [5 empty] | N | 57 | 58 | N
| N | 59 | 60 | N | [5 empty] | N | 59 | 60 | N
| N | 61 | 62 | N | [5 empty] | N | 61 | 62 | N
| N | 63 | 64 | N | [5 empty] | N | 63 | 64 | N
| N | 65 | 66 | N | [5 empty] | N | 65 | 66 | N
66 Circuit Master Panel - Bottom Fed | [8 empty] | 66 Circuit Slave Panel #1 - Bottom Fed
Utilizing 4 - 12 circuit control buses | [8 empty] | Utilizing 4 - 12 circuit control buses
| BUS POSITION |  |  | BUS POSITION | [5 empty] | BUS POSITION |  |  | BUS POSITION
|  | Ckt Number | Ckt Number | [7 empty] | Ckt Number | Ckt Number
| N | 1 | 2 | N | [5 empty] | N | 1 | 2 | N
| N | 3 | 4 | N | [5 empty] | N | 3 | 4 | N
| N | 5 | 6 | N | [5 empty] | N | 5 | 6 | N
| N | 7 | 8 | N | [5 empty] | N | 7 | 8 | N
| N | 9 | 10 | N | [5 empty] | N | 9 | 10 | N
| N | 11 | 12 | N | [5 empty] | N | 11 | 12 | N
|  | PHYSICAL GAP | [8 empty] | PHYSICAL GAP
NF12SBLG3 (A) | P | 13 | 14 | C | NF12SBRG3 (B) |  | P= Power Supply |  | NF12SBLG3 (E) |  | 13 | 14 |  | NF12SBRG3 (F)
| P | 15 | 16 | C |  |  | C= Controller |  |  |  | 15 | 16
| P | 17 | 18 | C |  |  | X= Slave Address selector |  |  |  | 17 | 18
| 1 | 19 | 20 | 1 |  |  | N=Non-controllable Breaker |  |  | 1 | 19 | 20 | 1
| 2 | 21 | 22 | 2 | [5 empty] | 2 | 21 | 22 | 2
| 3 | 23 | 24 | 3 | [5 empty] | 3 | 23 | 24 | 3
| 4 | 25 | 26 | 4 | [5 empty] | 4 | 25 | 26 | 4
| 5 | 27 | 28 | 5 | [5 empty] | 5 | 27 | 28 | 5
| 6 | 29 | 30 | 6 | [5 empty] | 6 | 29 | 30 | 6
| 7 | 31 | 32 | 7 | [5 empty] | 7 | 31 | 32 | 7
| 8 | 33 | 34 | 8 | [5 empty] | 8 | 33 | 34 | 8
| 9 | 35 | 36 | 9 | [5 empty] | 9 | 35 | 36 | 9
| 10 | 37 | 38 | 10 | [5 empty] | 10 | 37 | 38 | 10
| 11 | 39 | 40 | 11 | [5 empty] | 11 | 39 | 40 | 11
| 12 | 41 | 42 | 12 | [5 empty] | 12 | 41 | 42 | 12
NF12SBRG3 (D) | 12 | 43 | 44 | 12 | NF12SBLG3 (C) |  |  |  | NF12SBRG3 (H) | 12 | 43 | 44 | 12 | NF12SBLG3 (G)
| 11 | 45 | 46 | 11 | [5 empty] | 11 | 45 | 46 | 11
| 10 | 47 | 48 | 10 |  | Example: |  |  |  | 10 | 47 | 48 | 10 |  | Example:
| 9 | 49 | 50 | 9 |  | Circuit Number 50 |  |  |  | 9 | 49 | 50 | 9 |  | Circuit Number 50
| 8 | 51 | 52 | 8 |  | Bus C |  |  |  | 8 | 51 | 52 | 8 |  | Bus G
| 7 | 53 | 54 | 7 |  | Bus Position 9 |  |  |  | 7 | 53 | 54 | 7 |  | Bus Position 9
| 6 | 55 | 56 | 6 |  | Direct Breaker Control Manual Coil Register 06073 |  |  |  | 6 | 55 | 56 | 6 |  | Direct Breaker Control Manual Coil Register 06201
| 5 | 57 | 58 | 5 | [5 empty] | 5 | 57 | 58 | 5
| 4 | 59 | 60 | 4 | [5 empty] | 4 | 59 | 60 | 4
| 3 | 61 | 62 | 3 | [5 empty] | 3 | 61 | 62 | 3
| 2 | 63 | 64 | 2 | [5 empty] | 2 | 63 | 64 | 2
| 1 | 65 | 66 | 1 | [5 empty] | 1 | 65 | 66 | 1
|  |  |  | X | [8 empty] | X
|  |  |  | X | [8 empty] | X
|  |  |  | X | [8 empty] | X
84 Circuit Master Panel | [8 empty] | 84 Circuit Slave Panel #1
Utilizing 4 control buses | [8 empty] | Utilizing 4 control buses
| BUS POSITION |  |  | BUS POSITION | [5 empty] | BUS POSITION |  |  | BUS POSITION
|  | Ckt Number | Ckt Number | [7 empty] | Ckt Number | Ckt Number
NF18SBLG3 (A) | P | 1 | 2 | C | NF18SBRG3 (B) |  | P= Power Supply |  | NF18SBLG3 (E) |  | 1 | 2 |  | NF18SBRG3 (F)
| P | 3 | 4 | C |  |  | C= Controller |  |  |  | 3 | 4
| P | 5 | 6 | C | [6 empty] | 5 | 6
| 1 | 7 | 8 | 1 | [5 empty] | 1 | 7 | 8 | 1
| 2 | 9 | 10 | 2 | [5 empty] | 2 | 9 | 10 | 2
| 3 | 11 | 12 | 3 | [5 empty] | 3 | 11 | 12 | 3
| 4 | 13 | 14 | 4 | [5 empty] | 4 | 13 | 14 | 4
| 5 | 15 | 16 | 5 | [5 empty] | 5 | 15 | 16 | 5
| 6 | 17 | 18 | 6 | [5 empty] | 6 | 17 | 18 | 6
| 7 | 19 | 20 | 7 | [5 empty] | 7 | 19 | 20 | 7
| 8 | 21 | 22 | 8 | [5 empty] | 8 | 21 | 22 | 8
| 9 | 23 | 24 | 9 | [5 empty] | 9 | 23 | 24 | 9
| 10 | 25 | 26 | 10 | [5 empty] | 10 | 25 | 26 | 10
| 11 | 27 | 28 | 11 | [5 empty] | 11 | 27 | 28 | 11
| 12 | 29 | 30 | 12 | [5 empty] | 12 | 29 | 30 | 12
| 13 | 31 | 32 | 13 | [5 empty] | 13 | 31 | 32 | 13
| 14 | 33 | 34 | 14 | [5 empty] | 14 | 33 | 34 | 14
| 15 | 35 | 36 | 15 | [5 empty] | 15 | 35 | 36 | 15
| 16 | 37 | 38 | 16 | [5 empty] | 16 | 37 | 38 | 16
| 17 | 39 | 40 | 17 | [5 empty] | 17 | 39 | 40 | 17
| 18 | 41 | 42 | 18 | [5 empty] | 18 | 41 | 42 | 18
NF21SBRG3 (C) |  | PHYSICAL GAP |  |  | NF21SBLG3 (D) |  |  |  | NF21SBRG3 (G) |  | PHYSICAL GAP |  |  | NF21SBLG3 (H)
| 1 | 43 | 44 | 1 | [5 empty] | 1 | 43 | 44 | 1
| 2 | 45 | 46 | 2 | [5 empty] | 2 | 45 | 46 | 2
| 3 | 47 | 48 | 3 |  | Example: |  |  |  | 3 | 47 | 48 | 3 |  | Example:
| 4 | 49 | 50 | 4 |  | Circuit Number 50 |  |  |  | 4 | 49 | 50 | 4 |  | Circuit Number 50
| 5 | 51 | 52 | 5 |  | Bus D |  |  |  | 5 | 51 | 52 | 5 |  | Bus H
| 6 | 53 | 54 | 6 |  | Bus Position 4 |  |  |  | 6 | 53 | 54 | 6 |  | Bus Position 4
| 7 | 55 | 56 | 7 |  | Direct Breaker Control Manual Coil Register 06100 |  |  |  | 7 | 55 | 56 | 7 |  | Direct Breaker Control Manual Coil Register 06228
| 8 | 57 | 58 | 8 | [5 empty] | 8 | 57 | 58 | 8
| 9 | 59 | 60 | 9 | [5 empty] | 9 | 59 | 60 | 9
| 10 | 61 | 62 | 10 | [5 empty] | 10 | 61 | 62 | 10
| 11 | 63 | 64 | 11 | [5 empty] | 11 | 63 | 64 | 11
| 12 | 65 | 66 | 12 | [5 empty] | 12 | 65 | 66 | 12
| 13 | 67 | 68 | 13 | [5 empty] | 13 | 67 | 68 | 13
| 14 | 69 | 70 | 14 | [5 empty] | 14 | 69 | 70 | 14
| 15 | 71 | 72 | 15 | [5 empty] | 15 | 71 | 72 | 15
| 16 | 73 | 74 | 16 | [5 empty] | 16 | 73 | 74 | 16
| 17 | 75 | 76 | 17 | [5 empty] | 17 | 75 | 76 | 17
| 18 | 77 | 78 | 18 | [5 empty] | 18 | 77 | 78 | 18
| 19 | 79 | 80 | 19 | [5 empty] | 19 | 79 | 80 | 19
| 20 | 81 | 82 | 20 | [5 empty] | 20 | 81 | 82 | 20
| 21 | 83 | 84 | 21 | [5 empty] | 21 | 83 | 84 | 21
Control Bus Numbering – Column-Width Panelboards
A column-width panel is designed with a single-sided rail only, with breakers arranged in a single vertical column. This requires a control bus to be mounted upside-down at the bottom of the panel.
For the master panel, the bus with the Slave Address Selector or Power Supply is always the “A” bus. The bus with the Wiring Harness or Controller is always the "B" bus. Since master panels are built with the power supply located at the bottom, they will have the “B” bus at the top and the “A” bus at the bottom. Since slave panels are built with the slave address selector located at the bottom, they will require the same upside-down configuration. See example drawings below along with determining the modbus register.
|  | 30 Circuit Master Panel | [8 empty] | 30 Circuit Slave Panel #1
|  | Utilizing 2 - 12 circuit control buses | [8 empty] | Utilizing 2 - 12 circuit control buses
|  |  |  | BUS POSITION | [8 empty] | BUS POSITION
|  |  | Ckt Number | [8 empty] | Ckt Number
|  |  | 1 | C | NF12SBRG3 (B) |  |  | P= Power Supply |  |  |  | 1 |  | NF12SBRG3 (D)
|  |  | 2 | C |  |  |  | C= Controller |  |  |  | 2
|  |  | 3 | C |  |  |  | X= Slave Address selector |  |  |  | 3
|  |  | 4 | 1 | [7 empty] | 4 | 1
|  |  | 5 | 2 | [7 empty] | 5 | 2
|  |  | 6 | 3 | [7 empty] | 6 | 3
|  |  | 7 | 4 | [7 empty] | 7 | 4
|  |  | 8 | 5 | [7 empty] | 8 | 5
|  |  | 9 | 6 | [7 empty] | 9 | 6
|  |  | 10 | 7 | [7 empty] | 10 | 7
|  |  | 11 | 8 | [7 empty] | 11 | 8
|  |  | 12 | 9 | [7 empty] | 12 | 9
|  |  | 13 | 10 | [7 empty] | 13 | 10
|  |  | 14 | 11 | [7 empty] | 14 | 11
|  |  | 15 | 12 | [7 empty] | 15 | 12
|  |  | 16 | 12 | NF12SBLG3 (A) | [6 empty] | 16 | 12 | NF12SBLG3 (C)
|  |  | 17 | 11 | [7 empty] | 17 | 11
|  |  | 18 | 10 |  | Example: | [5 empty] | 18 | 10 |  | Example:
|  |  | 19 | 9 |  | Circuit Number 19 | [5 empty] | 19 | 9 |  | Circuit Number 19
|  |  | 20 | 8 |  | Bus A | [5 empty] | 20 | 8 |  | Bus C
|  |  | 21 | 7 |  | Bus Position 9 | [5 empty] | 21 | 7 |  | Bus Position 9
|  |  | 22 | 6 |  | Direct Breaker Control Manual Coil Register 06009 | [5 empty] | 22 | 6 |  | Direct Breaker Control Manual Coil Register 06073
|  |  | 23 | 5 | [7 empty] | 23 | 5
|  |  | 24 | 4 | [7 empty] | 24 | 4
|  |  | 25 | 3 | [7 empty] | 25 | 3
|  |  | 26 | 2 | [7 empty] | 26 | 2
|  |  | 27 | 1 | [7 empty] | 27 | 1
|  |  | 28 | P | [7 empty] | 28
|  |  | 29 | P | [7 empty] | 29
|  |  | 30 | P | [7 empty] | 30
|  | 42 Circuit Master Panel | [8 empty] | 42 Circuit Slave Panel #1
|  | Utilizing 2 - 18 circuit control buses | [8 empty] | Utilizing 2 - 18 circuit control buses
|  |  |  | BUS POSITION | [8 empty] | BUS POSITION
|  |  | Ckt Number | [8 empty] | Ckt Number
|  |  | 1 | C | NF18SBLG3 (B) |  |  | P= Power Supply |  |  |  | 1 |  | NF18SBLG3 (D)
|  |  | 2 | C |  |  |  | C= Controller |  |  |  | 2
|  |  | 3 | C |  |  |  | X= Slave Address selector |  |  |  | 3
|  |  | 4 | 1 | [7 empty] | 4 | 1
|  |  | 5 | 2 | [7 empty] | 5 | 2
|  |  | 6 | 3 | [7 empty] | 6 | 3
|  |  | 7 | 4 | [7 empty] | 7 | 4
|  |  | 8 | 5 | [7 empty] | 8 | 5
|  |  | 9 | 6 | [7 empty] | 9 | 6
|  |  | 10 | 7 | [7 empty] | 10 | 7
|  |  | 11 | 8 | [7 empty] | 11 | 8
|  |  | 12 | 9 | [7 empty] | 12 | 9
|  |  | 13 | 10 | [7 empty] | 13 | 10
|  |  | 14 | 11 | [7 empty] | 14 | 11
|  |  | 15 | 12 | [7 empty] | 15 | 12
|  |  | 16 | 13 | [7 empty] | 16 | 13
|  |  | 17 | 14 | [7 empty] | 17 | 14
|  |  | 18 | 15 | [7 empty] | 18 | 15
|  |  | 19 | 16 | [7 empty] | 19 | 16
|  |  | 20 | 17 | [7 empty] | 20 | 17
|  |  | 21 | 18 | [7 empty] | 21 | 18
|  |  | 22 | 18 | NF18SBRG3 (A) | [6 empty] | 22 | 18 | NF18SBRG3 (C)
|  |  | 23 | 17 | [7 empty] | 23 | 17
|  |  | 24 | 16 | [7 empty] | 24 | 16
|  |  | 25 | 15 | [7 empty] | 25 | 15
|  |  | 26 | 14 | [7 empty] | 26 | 14
|  |  | 27 | 13 | [7 empty] | 27 | 13
|  |  | 28 | 12 | [7 empty] | 28 | 12
|  |  | 29 | 11 | [7 empty] | 29 | 11
|  |  | 30 | 10 |  | Example: | [5 empty] | 30 | 10 |  | Example:
|  |  | 31 | 9 |  | Circuit Number 31 | [5 empty] | 31 | 9 |  | Circuit Number 31
|  |  | 32 | 8 |  | Bus A | [5 empty] | 32 | 8 |  | Bus C
|  |  | 33 | 7 |  | Bus Position 9 | [5 empty] | 33 | 7 |  | Bus Position 9
|  |  | 34 | 6 |  | Direct Breaker Control Manual Coil Register 06009 | [5 empty] | 34 | 6 |  | Direct Breaker Control Manual Coil Register 06073
|  |  | 35 | 5 | [7 empty] | 35 | 5
|  |  | 36 | 4 | [7 empty] | 36 | 4
|  |  | 37 | 3 | [7 empty] | 37 | 3
|  |  | 38 | 2 | [7 empty] | 38 | 2
|  |  | 39 | 1 | [7 empty] | 39 | 1
|  |  | 40 | P | [7 empty] | 40
|  |  | 41 | P | [7 empty] | 41
|  |  | 42 | P | [7 empty] | 42
|  | 42 Circuit Master Panel | [8 empty] | 42 Circuit Slave Panel #1
|  | Utilizing 2 - 21 circuit control buses | [8 empty] | Utilizing 2 - 21 circuit control buses
|  |  |  | BUS POSITION | [8 empty] | BUS POSITION
|  |  | Ckt Number | [8 empty] | Ckt Number
[5 empty] | NF21SBLG3 (B) |  |  | P= Power Supply | [5 empty] | NF21SBLG3 (D)
C= Controller
X= Slave Address selector
|  |  | 1 | C | [7 empty] | 1
|  |  | 2 | C | [7 empty] | 2
|  |  | 3 | C | [7 empty] | 3
|  |  | 4 | 1 | [7 empty] | 4 | 1
|  |  | 5 | 2 | [7 empty] | 5 | 2
|  |  | 6 | 3 | [7 empty] | 6 | 3
|  |  | 7 | 4 | [7 empty] | 7 | 4
|  |  | 8 | 5 | [7 empty] | 8 | 5
|  |  | 9 | 6 | [7 empty] | 9 | 6
|  |  | 10 | 7 | [7 empty] | 10 | 7
|  |  | 11 | 8 | [7 empty] | 11 | 8
|  |  | 12 | 9 | [7 empty] | 12 | 9
|  |  | 13 | 10 | [7 empty] | 13 | 10
|  |  | 14 | 11 | [7 empty] | 14 | 11
|  |  | 15 | 12 | [7 empty] | 15 | 12
|  |  | 16 | 13 | [7 empty] | 16 | 13
|  |  | 17 | 14 | [7 empty] | 17 | 14
|  |  | 18 | 15 | [7 empty] | 18 | 15
|  |  | 19 | 16 | [7 empty] | 19 | 16
|  |  | 20 | 17 | [7 empty] | 20 | 17
|  |  | 21 | 18 | [7 empty] | 21 | 18
|  |  | 22 | 18 | NF21SBRG3 (A) | [6 empty] | 22 | 18 | NF21SBRG3 (C)
|  |  | 23 | 17 | [7 empty] | 23 | 17
|  |  | 24 | 16 | [7 empty] | 24 | 16
|  |  | 25 | 15 | [7 empty] | 25 | 15
|  |  | 26 | 14 | [7 empty] | 26 | 14
|  |  | 27 | 13 | [7 empty] | 27 | 13
|  |  | 28 | 12 | [7 empty] | 28 | 12
|  |  | 29 | 11 | [7 empty] | 29 | 11
|  |  | 30 | 10 |  | Example: | [5 empty] | 30 | 10 |  | Example:
|  |  | 31 | 9 |  | Circuit Number 31 | [5 empty] | 31 | 9 |  | Circuit Number 31
|  |  | 32 | 8 |  | Bus A | [5 empty] | 32 | 8 |  | Bus C
|  |  | 33 | 7 |  | Bus Position 9 | [5 empty] | 33 | 7 |  | Bus Position 9
|  |  | 34 | 6 |  | Direct Breaker Control Manual Coil Register 06009 | [5 empty] | 34 | 6 |  | Direct Breaker Control Manual Coil Register 06073
|  |  | 35 | 5 | [7 empty] | 35 | 5
|  |  | 36 | 4 | [7 empty] | 36 | 4
|  |  | 37 | 3 | [7 empty] | 37 | 3
|  |  | 38 | 2 | [7 empty] | 38 | 2
|  |  | 39 | 1 | [7 empty] | 39 | 1
|  |  | 40 | P | [7 empty] | 40
|  |  | 41 | P | [7 empty] | 41
|  |  | 42 | P | [7 empty] | 42
|  |  |  | X | [8 empty] | X
|  |  |  | X | [8 empty] | X
|  |  |  | X | [8 empty] | X
PS + Controller SEL = 1 SEL = 2 SEL = 3
SEL = 4 SEL = 5 SEL = 6 SEL = 7
1
2
3
6
5
A
B
C
D
E
F
G
H
I
J
K
L
M
N
O
P
0